## Definitions
Keyword | Explanation
ASHRAE 62.1-2010, Section 5 - "Systems and Equipment." | Key Responsibilities of AHU Manufacturers under ASHRAE 62.1-2010 Section 5 | ✅ ASHRAE 62.1 Compliance Points for AHU Manufacturers
| 1. Ventilation Air Distribution (5.2) | 1. Ventilation Air Distribution (§5.1)
AHUs must be capable of delivering the required minimum outdoor air to all occupied zones.
| Documentation should include airflow capacities, damper control strategies, and zoning capabilities. | Ensure proper airflow paths and distribution effectiveness.
| 2. Ventilation System Controls (5.4) | Support for air balancing and control.
| AHUs should support control systems that regulate outdoor air intake based on occupancy and demand. | 2. Exhaust Duct Location (§5.2)
Manufacturers must provide control logic and integration capabilities (e.g., BACnet, Modbus).
| 3. Particulate Matter Removal (5.9) | Design to prevent re-entrainment of exhaust air.
| AHUs must include filters rated MERV 6 or higher. | 3. Ventilation System Controls (§5.3)
Product data should specify filter type, rating, and replacement procedures.
| 4. Drain Pans (5.11) | Capability for demand-controlled ventilation (DCV).
| AHUs must have sloped drain pans to prevent standing water and microbial growth. | Integration with sensors (e.g., CO₂, occupancy).
| Documentation should include pan design, slope angle, and materials. | 4. Airstream Surfaces (§5.4)
5. Finned-Tube Coils and Heat Exchangers (5.12)
| AHUs must allow access for cleaning and include drain pans under coils. | Use of materials resistant to:
| Manufacturer drawings should show access panels and maintenance pathways. | Mold growth.
Erosion from airflow.
| 6. Access for Maintenance (5.14) | 5. Outdoor Air Intakes (§5.5)
AHUs must be designed for easy access to filters, coils, fans, and dampers.
| Include exploded views or maintenance access diagrams in submittals. | Design features to prevent:
| 7. Outdoor Air Intakes (5.6) | Water intrusion.
| While placement is typically a design responsibility, AHU manufacturers must ensure intake configurations support proper filtration and protection (e.g., bird screens, louvers). | Snow entrainment.
Bird entry.
| 📄 Documentation to Provide | 6. Local Capture of Contaminants (§5.6)
1. AHU technical datasheets showing airflow rates, filter ratings, and control capabilities.
| 2. Installation manuals detailing access for maintenance and cleaning. | Support for source capture systems (e.g., return/exhaust configurations).
| 3. Compliance statement referencing ASHRAE 62.1-2010 Section 5. | 7. Ozone Generating Devices (§5.7)
4. Filter specifications with MERV ratings.
| 5. Drain pan and coil design drawings. | No ozone-generating components unless compliant with emission limits.
6. Control system integration guides.
Conduit | a tube or trough for protecting electric wiring

## Eurovent Ratings
Brand | Range | Model | Panel Thickness | Insulation | Profile Type | MB - Casing Strength CS class | MB - Casing Air Leakage CAL class @ -400 Pa | CAL Class @ +700 Pa | MB - Filter Bypass Leakage FBL class | MB - Thermal Transmittance | MB - Thermal Bridging Factor | Factory city
DAIKIN | D-AHU | Energy F2 New | 42 mm | Foam | Natural | D1(M) | L1(M) | L1(M) | F9(M) | T3 | TB4 | Dubai, Riyadh
DAIKIN | D-AHU | Energy S2 New | 62 mm | Foam | Natural | D1(M) | L1(M) | L1(M) | M6(M) | T3 | TB4 | Dubai, Riyadh
DAIKIN | D-AHU | Energy TermiC° F2 New | 42 mm | Foam | Natural TB | D1(M) | L1(M) | L1(M) | F9(M) | T2 | TB2 | Dubai, Riyadh
DAIKIN | D-AHU | Energy TermiC° S2 New | 62 mm | Foam | Natural TB | D1(M) | L1(M) | L1(M) | F9(M) | T2 | TB2 | Dubai, Riyadh
DAIKIN | D-AHU | Sound F2 | 42 mm | Mineral Wool | Natural | D2(M) | L1(M) | L1(M) | M6(M) | T3 | TB4 | Dubai, Riyadh
DAIKIN | D-AHU | Sound S2 | 62 mm | Mineral Wool | Natural | D2(M) | L1(M) | L3(M) | F9(M) | T3 | TB3 | Dubai, Riyadh
DAIKIN | D-AHU | Sound TermiC° F2 | 42 mm | Mineral Wool | Natural TB | D1(M) | L1(M) | L2(M) | F9(M) | T2 | TB2 | Dubai, Riyadh
DAIKIN | D-AHU | Sound TermiC° S2 | 62 mm | Mineral Wool | Natural TB | D1(M) | L1(M) | L2(M) | F9(M) | T2 | TB2 | Dubai, Riyadh

## ASHRAE 62.1
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
1.1 | SUMMARY
A. | Read this Section in conjunction with other related Divisions, the General Requirements, the Particular Specification, Schedules, Drawings and the Contract Conditions. | Noted | IOM manuals are provided

## AMCA Ratings
TO Filter Suppliers | TO Coil Suppliers | TO fan Suppliers
|  | Air Movement and Control Association International, Inc. | Remark
AMCA 99-2408 Operating Limits for Centrifugal Fans. (AMCA 99-86: Standards Handbook)
AMCA 210 Laboratory Methods of Testing Fans for Aerodynamic Performance Rating (ANSI)
AMCA 300 Reverberant Room Method for Sound Testing of Fans
AMCA 301: Methods for Calculating Fan Sound Ratings from Laboratory Test Data
AMCA 500-DLaboratory Methods of Testing Dampers for Rating
Operating Limits: AMCA 99 or equivalent relevant BS/EN standards.

## 1. General
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
1.1 | SUMMARY
A. | Read this Section in conjunction with other related Divisions, the General Requirements, the Particular Specification, Schedules, Drawings and the Contract Conditions. | Noted | IOM manuals are provided
B. | Section Includes
1 | Air handling units. | Noted | DAIKIN AHUs are provided
2 | The mechanical Services particular specification, drawings and schedules. | In Contractor's scope | DAIKIN AHUs are provided
C. | Related Divisions and Documentation
1 | Division 22 Plumbing Work Sections. | In Contractor's scope | DAIKIN AHUs are provided
2 | Division 23 HVAC Work Sections. | In Contractor's scope | DAIKIN AHUs are provided
3 | Division 26 Electrical Work Sections | In Contractor's scope | DAIKIN AHUs are provided
D. | General:
1 | Air handling unit (AHU) shall mean an assembly of packaged plant components. | Comply | DAIKIN AHUs integrates all necessary components, designed and assembled to function as a complete system in accordance with the project Schedule/Tender documents
2 | The duties and performance of the units shall be in accordance with the details indicated elsewhere and include any allowance required to meet manufacturing tolerances. | Comply | Duties and performance of the DAIKIN AHUs shall be in accordance with the specifications and requirements detailed in the Schedule/Tender documents
3 | Individual components shall, in addition to the requirements of this section, comply with other relevant sections of this specification. | Comply | Duties and performance of the DAIKIN AHUs shall be in accordance with the specifications and requirements detailed in the Schedule/Tender documents
4 | Air handling units shall be fully assembled and tested at the manufacturer’s works to demonstrate that aerodynamic performance, air leakage, air flow, design resistance and noise levels are in compliance with the specification and performance requirements. The results and a compliance statement shall be submitted to the CA prior to delivery to site. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided if required 3. Quality Control report will be provided during the time of delivery.
1.2 | SUMMARY
A. | Drawings and general provisions of the Contract, including Conditions of Contract and Division 01 Specification Sections, apply to this Section. | In Contractor's scope | DAIKIN AHUs are provided
A. | This Section includes requirements for materials and installation of air handling units, including accessory items. | Noted | DAIKIN AHUs are provided
A. | The Contractor shall submit drawings that include the following in addition to all engineer’s requirements: | In Contractor's scope | DAIKIN AHUs are provided
| • Locations of air handling units. | In Contractor's scope
| • Type of air handling units. | In Contractor's scope | DAIKIN shall provide AHU datasheets are provided
| • Installation details and manufacturer's catalogue information on each type of air handling units used. | Noted | DAIKIN shall provide AHU datasheets and IOM manuals
| • Certifications and listings of the air handling units. | Noted | DAIKIN shall provide AHU datasheets and necessary certifications can be submitted along with submittal
1.3 | GENERAL REQUIREMENTS
A. | Manufacturer's selections shall be subject to approval by the Engineer. Air Handling unit manufacturers and the specific unit models shall be Eurovent certified and in accordance with the requirements of ENI 886. | Comply with Remarks | DAIKIN AHUs are Eurovent certified
B. | The duties and performance of the units shall be in accordance with the details indicated elsewhere and include any allowance required to meet manufacturing tolerances. | Comply | DAIKIN AHUs are selected as per scheduled data
C. | Individual components shall, in addition to the requirements of this section, comply with other relevant sections of this specification. | Comply | DAIKIN AHUs are selected as per scheduled data
D. | Air handling units shall be fully assembled and tested at the manufacturer's works to demonstrate that aerodynamic performance, leakage air flow, design resistance and noise levels are in compliance with the specification and performance requirements. | In Contractor's scope | 1. AHUs shall be assembled & commissioned at site by installing contractor 2. Factory Acceptance Test can be provided if required | Remove FAT if price not considered in quotation
E. | The results and a compliance statement shall be submitted to the Engineer prior to delivery to site. | Comply | DAIKIN AHUs are selected as per scheduled data
F. | The contractor shall provide suitable bases and anti-vibration measures as required in the relevant sections of the specification. | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
G. | The contractor shall provide power supplies form DBS to all internal AHU lighting and small power supplies. The AHUs lighting and small power systems shall be prewired at the factory to an isolator mounted in the unit. | Comply | DAIKIN AHUs shall be factory fitted internal wiring and lights | Not Comply if selected w/o bulb and w/o wiring 1. Light mounted and factory wired till externally mounted on/off switch with bulb (6W led bulb Illumination 60 W). 2. Each light will be provided with switch. 3. Light shall be vapour proof, refer catalogue 4. Plastic flexible conduit shall be IP66 rated 5. Switch & light shall be IP55 rated
H. | The cooling medium is chilled water with the air handling unit cooling coil to be provided with a pressure independent modulating 2-port control valve as indicated on the drawings. The cooling coil shall be provided with stainless steel condensate drain pans and borosilicate condensate traps of sufficient depth of seal to match the internal operating static pressures. | In Contractor's scope | Valves and condensate Traps shall be provided by the contractor. DAIKIN AHUs are provided with SS Drain Pan.
| The Contractor shall replace all air handling unit filters with new panel and bag filters in accordance with the equipment schedules, supplied by the air handling unit manufacturer post commissioning and prior to handover. Return air openings shall be projected during construction with Merv 13. | In Contractor's scope | DAIKIN AHUs are provided with filters as mentioned in the schedules.
J. | The Contractor shall allow for one complete belt/pulley change for fan, to be changed subject to the provision of satisfactory commissioning results (the submitted commissioning figures shall demonstrate that measured air-flow rates are in accordance with the design flow rates). | In Contractor's scope | DAIKIN AHUs are supplied with factory-assembled fans, motors, and pulley configurations designed to deliver the airflow rates specified in the schedule
K. | Fresh air and exhaust connections shall be provided with tight shut-off dampers arranged to close when the system shuts down unless otherwise stated. | In Contractor's scope
L. | All necessary penetrations in the air handling unit casing e.g. to accommodate controls items etc, shall be undertaken at the factory. Penetrations shall not be permitted on site. | Comply | All necessary Tapping Points are provided as per inputs during manufacturing stage. | Factory can provide all necessary Penetrations marked by client during GA drawing approval
M. | The AHUs shall be provided with Variable frequency drives (VFDs) on all fan motors. | Comply | If required, VFDs can be provided | DO not comply if VFDs are not selected Not Applicable for EC plug fans
1.4 | RELATED DOCUMENTS
A. | Drawings and general provisions of the Contract, including Conditions of Contract and Division 1 Specification Sections, apply to this Section. | In Contractor's scope
1.4.1 | SUMMARY
A. | This Section includes constant or variable -volume, central-station air-handling units with coils for indoor or outdoor installations as applicable. | Noted | DAIKIN AHUs are provided
B. | Provide fans and motors capable of stable operation at design conditions and at design cubic meters per minute (cubic feet per minute) and 110 percent pressure as stated above. | Comply with Remarks | AHUs are selected at scheduled data. Fan data is provided in AHU datasheet | If specifically required to comply, then we might need to select AHUs at 110% Pressure Drop or Airflow as instructed in schedule/specs
C. | Lower than design pressure drop of approved individual components may allow use of a smaller fan motor and still provide the safety factor. When submitted as a deviation, a smaller motor may be approved in the interest of energy conservation. Such a deviation shall not qualify for any value engineering incentive claim or reward. | Comply | AHUs are selected at scheduled data. Fan data is provided in AHU datasheet
D. | Select fan operating point to right hand side of peak static pressure point and near the peak of static efficiency. | Comply | Fan curves are shown on AHU datasheet
E. | Operating Limits: AMCA 99 or equivalent relevant BS/EN standards. | Noted | 1. Fan curves as per our technical data 2. Unit shall be manufactured, rated, tested and certified in accordance with EN13053 (Rating and performance for unit's components and section) and EN1886 (Mechanical Performance). 3. Fans are AMCA 210 certified. | Check for AMCA certification for fan models when working on a project, else remove point 3.
1.4.2 | PERFORMANCE REQUIREMENTS
A. | Delegated Design: Design vibration isolation and seismic-restraint details, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
B. | Structural Performance: Casing panels shall be self-supporting and capable of withstanding 133 percent of internal static pressures indicated, without panel joints exceeding a deflection of L/200 where "L" is the unsupported span length within completed casings. | Comply | DAIKIN AHUs shall be with D1 casing strength in accordance with Eurovent EN1886 | Eurovent Ratings
C. | Seismic Performance: Air-handling units shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7]. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
1. | The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified." | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
1.4 | SECTION INCLUDES
A. | Casing construction.
B. | Fan section.
C. | Coil section.
D. | Humidifier section.
E. | Filter and air cleaner section.
F. | Damper section.
G. | Access section.
H. | Controls.
I. | Roof mounting curb.
1.4.1 | RELATED REQUIREMENTS
A. | Section 21 07 19 - Fire Suppression Piping Insulation.
B. | Section 22 10 05 - Plumbing Piping: Equipment drains.
C. | Section 23 05 13 - Common Motor Requirements for HVAC Equipment.
D. | Section 23 05 48 - Vibration and Seismic Controls for HVAC.
E. | Section 23 05 93 - Testing, Adjusting, and Balancing for HVAC.
F. | Section 23 07 19 - HVAC Piping Insulation.
G. | Section 23 33 00 - Air Duct Accessories: Flexible duct connections.
H. | Section 23 34 13 - Axial HVAC Fans.
I. | Section 23 34 16 - Centrifugal HVAC Fans.
J. | Section 23 40 00 - HVAC Air Cleaning Devices.
K. | Section 23 84 13 - Humidifiers.
L. | Section 23 84 15 - Steam Humidifiers.
M. | Section 25 14 00 - Integrated Automation Local Control Units.
N. | Section 25 15 00 - Integrated Automation Software.

## 2. References
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
2.1 | REFERENCES
A. | SASO – Saudi Arabian Standards Organization
1 | SASO 1302 Air ducts for air conditioning - Part 1: Definitions, classification and terminology | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
2 | SASO 1434 Thermal environmental conditions for human occupancy. | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
3 | SASO 1435 Safety requirements for the installation on air conditioning and ventilating systems - Part 1: Definitions and technical terms. | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
4 | SASO 1436 Safety requirements for the installation on air conditioning and ventilating systems - Part 2: Requirements of HVAC systems. | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
5 | SASO 772 Code of practice for mechanical ventilation and air conditioning in buildings -Part 1: General basis of design. | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
6 | SASO 773 Code of practice for mechanical ventilation and air conditioning in buildings -Part 2: General requirements for installation. | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
B. | Air-Conditioning, Heating & Refrigeration Institute
| AHRI 410 Forced-Circulation Air-Cooling and Air-Heating Coils | Comply | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
| AHRI 430 Central-Station Air-Handling Units | Noted | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
C. | Air Movement and Control Association International, Inc.
| AMCA 99-2408 Operating Limits for Centrifugal Fans. (AMCA 99-86: Standards Handbook) | Noted | AMCA 210 certified fans can be provided
| AMCA 210 Laboratory Methods of Testing Fans for Aerodynamic Performance Rating (ANSI) | Noted | AMCA 210 certified fans can be provided(EC Plug are not AMCA Certified)
| AMCA 300 Reverberant Room Method for Sound Testing of Fans | Noted | AMCA 210 certified fans can be provided(EC Plug are not AMCA Certified)
| AMCA 301: Methods for Calculating Fan Sound Ratings from Laboratory Test Data | Noted | AMCA 210 certified fans can be provided(EC Plug are not AMCA Certified)
| AMCA 500-DLaboratory Methods of Testing Dampers for Rating | Noted | AMCA 210 certified fans can be provided(EC Plug are not AMCA Certified)
D. | American Society of Civil Engineers/Structural Engineering Institute
ASCE/SEI 7 Minimum Design Loads for Buildings and Other Structures
E. | American Society of Heating, Refrigerating and Air-Conditioning Engineers
ASHRAE 33Methods of Testing Forced Circulation Air Cooling and Air Heating Coils
ASHRAE 52.1Gravimetric and Dust-Spot Procedures for Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter
ASHRAE 52.2Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size (ANSI)
ASHRAE 62.1Ventilation for Acceptable Indoor Air Quality (ANSI)
F. | American Society of Heating, Refrigerating and Air-Conditioning Engineers/Illuminating Engineering Society of North America
ASHRAE/IESNA 90.1 Energy Standard for Buildings except Low-Rise Residential Buildings (ANSI)
G. | ASME International
ASME N510 Testing of Nuclear Air Treatment Systems
H. | ASTM International
ASTM A 666 Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar
ASTM B 88 Specification for Seamless Copper Water Tube
ASTM B 88M Specification for Seamless Copper Water Tube Metric
ASTM C 916 Specification for Adhesives for Duct Thermal Insulation
ASTM C 1071 Specification for Fibrous Glass Duct Lining Insulation (Thermal and Sound Absorbing Material)
National Electrical Manufacturers Association
NEMA AB 1 Molded Case Circuit Breakers, Molded Case Switches, and CircuitBreaker Enclosures
NEMA ICS 2 Industrial Control and Systems: Controllers, Contactors, and
Overload Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC
NEMA MG 1 Motors and Generators
J. | NFPA
NFPA 70 National Electrical Code
NFPA 90A Installation of Air Conditioning and Ventilating Systems
K. | Sheet Metal and Air Conditioning Contractors' National Association
HVAC Duct Construction Standards.
L. | Underwriters Laboratories Inc.
UL 181 Factory-Made Air Ducts and Air Connectors
UL 586 High-Efficiency, Particulate, Air Filter Units
UL 1995 Heating and Cooling Equipment
M. | EUROVENT: All relevant standards as applicable
2.2 | REFERENCES
A. | BS 4856 Methods for testing and rating fan coil units, unit heaters and unit coolers
B. | BS 7671:2008+A1:2011 – Requirements for electrical installations. IEE Wiring Regulations. Seventeenth edition.
C. | EUROVENT EN 1397: 2015 - Thermal & Airflow Test: Heat Exchangers - Hydronic Room Fan Coil Units
D. | EUROVENT EN 16583: 2015 – Sound Power Test: Heat Exchangers - Hydronic Room Fan Coil Units
E. | ASHRAE Compliance: Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Start-up."
F. | IESNA/ASHRAE 90.1 Compliance: Applicable requirements in IESNA/SHRAE 90.1,
Section 6 - "Heating, Ventilating, and Air-Conditioning."
2.3 | REFERENCES
A. | Codes and standards applicable to this section shall be primarily British Standards/ European Norms and United States Codes, unless otherwise specified, the performance/manufacturing standards of items mentioned in this section shall confirm to the applicable portions of the latest editions of the following codes, standards and regulations.
Reference Code Abbreviation Applicable Standard Title of Standard
American Society of Heating Refrigerating and Air Conditioning Engineers. ASHRAE -- --
National Electrical Manufacturers Association NEMA -- --
National Electrical Code NEC Section 424 --
Air Moving and Conditioning Associations AMCA -- --
National Fire Protection Association
NFPA NFPA 90A Standard for Air
Conditioning and
Ventilation
Systems
American Refrigeration Institute.
ARI -- --
European standards/ Norms EN -- --
B. | All HVAC equipment’s, pipes, valves and motors shall comply with the relevant SASO standards as applicable.
2.4 | REFERENCES
A. | BS 848-1 (ISO 5801) - Fans for general purposes. Performance using standardized airways.
B. | BS EN 12451 - Copper and copper alloys. Seamless, round tubes for heat exchangers
C. | BS ISO 13347 - Industrial fans. Determination of fan sound power levels under standardized laboratory conditions
D. | BS EN ISO 5136 - Acoustics. Determination of sound power radiated into a duct by fans and other air moving devices. In-duct method.
E. | PD 5304 - Safe use of machinery
F. | BS EN 60529 - Specification for degrees of protection provided by enclosures (IP code)
G. | BS 5141-1 - Specification for air heating and cooling coils. Method of testing for rating of cooling coils.
H. | BS 5141-2 - Specification for air heating and cooling coils. Method of testing for rating of heating coils. BS EN 10226-1 (BS 21) - Pipe threads where pressure tight joints are made on threads. Taper external threads and parallel internal threads. Dimensions, tolerances and designation.
J. | BS EN 1092 - Flanges and their joints.
K. | BS EN ISO 1461 - Hot dip galvanized coatings on fabricated iron and steel articles. Specifications and test methods.
L. | BS EN 779 - Particulate air filters for general ventilation. Determination of the filtration performance.
M. | BS 5588-9 - Fire precautions in the design, construction and use of buildings. Code of practice for ventilation and air conditioning ductwork.
N. | BS 476-4 - Fire tests on building materials and structures. Non-combustibility test for materials
O. | HSE L8 - Legionnaires' disease. The control of legionella bacteria in water systems. Approved Code of Practice.
P. | CIBSE TM 13- Minimising risk of legionnaires' disease NFPA Compliance:
Q. | NFPA 90A and NFPA 90B.
R. | Comply with UL 1995.
S. | Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.
2.5 | REFERENCES
A. | ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings; 2015, or latest edition.
B. | ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings; 2014, or latest edition.
C. | AHRI 260 - Sound Rating of Ducted Air Moving and Conditioning Equipment; 2017, or latest edition.
D. | AHRI 430 (I-P) - Performance Rating of Central Station Air-Handling Unit Supply Fans ; 2014, or latest edition.
E. | AHRI 1060 I-P - Performance Rating of Air-to-Air Heat Exchangers for Energy Recovery Ventilation Equipment; 2018, or latest edition.
F. | AMCA (DIR) - [Directory of] Products Licensed Under AMCA International Certified Ratings Program; http://www.amca.org/certified/search/company.aspx.
G. | AMCA 99 - Standards Handbook; 2016, or latest edition.
H. | AMCA 210 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating; 2016, or latest edition.
I. | AMCA 300 - Reverberant Room Method for Sound Testing of Fans; 2014, or latest edition.
J. | AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data; 2014, or latest edition.
K. | AMCA 500-L - Laboratory Methods of Testing Louvers for Rating; 2015, or latest edition.
L. | ASHRAE Std 52.2 - Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size; 2017, or latest edition.
M. | ASHRAE Std 62.1 - Ventilation For Acceptable Indoor Air Quality; 2019, or latest edition.
N. | ASTM E477 - Standard Test Method for Measuring Acoustical and Airflow Performance of Duct Liner Materials and Prefabricated Silencers; 2013, or latest edition.
O. | AHRI 410 - Standard for Forced-Circulation Air-Cooling and Air-Heating Coils; AirConditioning, Heating, and Refrigeration Institute; 2001 (R2011), or latest edition.
P. | AHRI 430 - Performance Rating Of Central Station Air-Handling Unit Supply Fans; 2014, or latest edition.
Q. | AHRI 610 - Performance Rating of Central System Humidifiers for Residential Applications; Air-Conditioning, Heating, and Refrigeration Institute; 2014, or latest edition.
R. | NEMA MG 1 - Motors and Generators; 2016, or latest edition.
S. | BS/EN 7671 - The IET Wiring Regulations, latest edition.
T. | NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems; 2018, or latest edition.
U. | UL (DIR) - Online Certifications Directory; current listings at database.ul.com.
V. | UL 153 – Standard for Portable Electric Luminaries; 2014, or latest edition.
W. | UL 181 - Standard for Factory-Made Air Ducts and Air Connectors; 2013, or latest edition.
X. | UL 508 – Standard for Industrial Control Equipment; Underwriters Laboratories Inc; 2018.
Y. | SMACNA (DCS) - HVAC Duct Construction Standards - Metal and Flexible; Sheet Metal and Air Conditioning Contractors' National Association; 2005, or latest edition.
Z. | UL (EAUED) - Electrical Appliance and Utilization EqOk, sdhall uipment Directory; Underwriters Laboratories Inc.; current edition.
AA. | UL 1598 - Luminaires; 2018, or latest edition.
BB. | UL 1812 – Standard for Ducted Heat Recovery Ventilators; 2013.
AC. | UL 1995 - Heating and Cooling Equipment; 2015, or latest edition.
CC. | Electricity Wiring Regulations latest edition.
DD. | ASHRAE Std 90.1 - Energy Standard for Buildings Except Low-Rise Residential Buildings; 2019, or latest edition.
ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings; 2015.
ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings; 2014.
2.6 | REFERENCE STANDARDS
A. | ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings; 2014 (Reaffirmed 2020).
B. | ACGIH - Ultraviolet Radiation: TLV(R) Physical Agents 7th Edition Documentation; 2010.
C. | AHRI 260 (I-P) - Sound Rating of Ducted Air Moving and Conditioning Equipment; 2017.
D. | AHRI 261 (SI) - Sound Rating of Ducted Air Moving and Conditioning Equipment; 2017.
E. | AHRI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils; 2001, with Addenda(2011).
F. | AHRI 430 (I-P) - Performance Rating of Central Station Air-handling Unit Supply Fans;2020
G. | AHRI 610 (I-P) - Performance Rating of Central System Humidifiers for Residential Applications; 2014.
H. | AHRI 611 (SI) - Performance Rating of Central System Humidifiers for Residential Applications; 2014.
I. | AHRI 1060 (I-P) - Performance Rating of Air-to-Air Exchangers for Energy Recovery Ventilation Equipment; 2023.
J. | AMCA (DIR) - (Directory of) Products Licensed Under AMCA International Certified Ratings Program; 2015.
K. | AMCA 99 - Standards Handbook; 2016.
L. | AMCA 210 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating; 2016, with Errata (2018).
M. | AMCA 300 - Reverberant Room Method for Sound Testing of Fans; 2014.
N. | AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data; 2022.
O. | AMCA 500-D - Laboratory Methods of Testing Dampers for Rating; 2018.
P. | AMCA 500-L - Laboratory Methods of Testing Louvers for Rating; 2023.
Q. | AMCA 611 - Certified Ratings Program - Product Rating Manual for Airflow Measurement Stations; 2015.
R. | ASHRAE Std 52.2 - Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size; 2017, with Addendum (2022).
S. | ASHRAE Std 62.1 - Ventilation for Acceptable Indoor Air Quality; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.
T. | ASHRAE Std 90.1 I-P - Energy Standard for Buildings Except Low-Rise Residential Buildings; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.
U. | ASHRAE Std 135 - A Data Communication Protocol for Building Automation and Control Networks; 2020, with Errata (2023).
V. | ASTM B177/B177M - Standard Guide for Engineering Chromium Electroplating; 2011 (Reapproved 2021).
W. | ASTM E477 - Standard Test Method for Laboratory Measurements of Acoustical and Airflow Performance of Duct Liner Materials and Prefabricated Silencers; 2020.
X. | Bluetooth CS - Bluetooth Core Specification; 2016, Addendum 2017.
Y. | IEEE 802.11 - IEEE Standard for Information Technology--Telecommunications and Information Exchange between Systems - Local and Metropolitan Area Networks--Specific Requirements - Part 11: Wireless LAN Medium Access Control (MAC) and Physical Layer (PHY) Specifications; 2020 (Corrigendum 2022).
Z. | IEEE 802.15.4 - IEEE Standard for Low-Rate Wireless Networks; 2020, with Corrigendum (2022).
AA. | LonMark Interoperability Guide - LonMark Application-Layer Interoperability Guide and LonMark Layer 1-6 Interoperability Guide; Version 3.4; 2005.
BB. | Modbus (PS) - The Modbus Organization Communications Protocol.; Latest Update.
CC. | NEMA MG 1 - Motors and Generators; 2021.
DD. | NFPA 70 - National Electrical Code; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.
EE. | NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems; 2024.
FF. | UL (DIR) - Online Certifications Directory; Current Edition.
GG. | UL 153 - Portable Electric Luminaries; Current Edition, Including All Revisions.
HH. | UL 181 - Standard for Factory-Made Air Ducts and Air Connectors; Current Edition,Including All Revisions.
II. | UL 508 - Industrial Control Equipment; Current Edition, Including All Revisions.
JJ. | UL 508A - Industrial Control Panels; Current Edition, Including All Revisions.
KK. | UL 795 - Commercial-Industrial Gas Heating Equipment; Current Edition, Including All Revisions.
LL. | UL 1598 - Luminaires; Current Edition, Including All Revisions.
MM.UL 1812 - Ducted Heat Recovery Ventilators; Current Edition, Including All Revisions.
NN. | UL 1995 - Heating and Cooling Equipment; Current Edition, Including All Revisions.

## 3. Submittals
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
3.1 | SUBMITTALS
A. | General: Comply with the requirements of Section 230010 Submittal Procedures and as stated elsewhere and submit the following. | Noted
B. | Technical Submittals:
1 | Submit manufacturer’s technical product data sheet for all AHU components, indicating unit construction, dimensions, weights, performance and maintenance requirements. | Comply with Remarks | DAIKIN shall submit all technical product datasheets for all AHU components, including unit construction, dimensions, weights, performance. IOM manual shall be provided for maintenance requirements.
2 | Submit a detailed equipment schedule, for each Air Handling Unit. | Comply | Technical product datasheet shall contain necessary details for individual AHUs
3 | Submit the following information, where applicable, to the CA for approval in accordance with the requirements of this specification: | Noted
a. | Schedule of starting and full load currents | In Contractor's scope | AHU electric load shall be mentioned on datasheet
b. | Details of connections for fans | In Contractor's scope | AHU IOM manuals are provided for electrical connections
c. | Fan characteristic curves with operating point clearly indicated. Fan curves shall indicate air volume, static pressure, fan speed and absorbed power. | Comply | Fan curves are shown on AHU datasheet
d. | Sound pressure spectrums | Comply | Fan/Motor sound data provided in the AHU datasheet based on measurements taken in a free field environment and spherical propagation
e. | Vibration mounting details, including isolation efficiency on high and low speed | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
f. | Coil pressure drops, air side and water side | Comply | Coil data is provided in AHU datasheet
g. | Coil air on and air off conditions | Comply | Coil data is provided in AHU datasheet
h. | Coil water on and water off temperatures | Comply | Coil data is provided in AHU datasheet
i. | Fan motor rating and design absorbed power | Comply | Fan Motor data is provided in AHU datasheet
j. | Fan and motor speeds | Comply | Fan Motor data is provided in AHU datasheet
k. | Drive belt sizes | Comply with Remarks | Drive sizes can be provided at the time of delivery
l. | Filter sizes and efficiencies | Comply | Filter details and sizes are provided in AHU datasheet
m. | Fan static and total pressures | Comply | Fan data is provided in AHU datasheet
n. | External to unit, static and total pressures | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
o. | Heat recovery details (i.e. thermal wheels, plate heat exchangers, etc.) | Comply | AHU datasheet includes all relevant data required for various components
p. | Humidifier model and rating | Comply | AHU datasheet includes all relevant data required for various components
q. | Attenuator insertion losses | In Contractor's scope
r. | All AHU accessories (i.e. volume control dampers, pressure gauges, etc.) | In Contractor's scope | Details of the components within the AHU are provided in the datasheet
4 | Provide predicted sound power levels for all openings including, fresh air intake, supply air, return air and exhaust air openings and casing radiated noise as indicated per the unit drawings and equipment schedules. | In Contractor's scope | Fan/Motor sound data provided in the AHU datasheet based on measurements taken in a free field environment and spherical propagation
5 | Submit maximum vibration levels for the assembled units at the points indicated for each unit where the unit structure integrates with the building support structure. At a minimum, vibration levels shall not exceed 50dB re 1 micro G at 1/ 3 octave band readings from 5Hz to 100Hz frequency. | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
6 | Submit details of Variable Speed Drive units including manufacturer's details. | In Contractor's scope
C. | Manufacturers Certified Drawings.
1 | Manufacturers certified drawings shall be provided for every AHU. The drawing information shall include | Comply | AHU datasheet includes all relevant data required for various components
a. | Unit Model | same as above
b. | Unit arrangement | same as above
c. | Information on all external connections | same as above
d. | Information on overall sizes | same as above
e. | Overall operating weight, and sizes, sections weight, point of supported weight load, | same as above
f. | Unit construction details and thermal break unit construction detail. | same as above
g. | Fan Selection Data: | same as above
h. | Cooling, Heating and Heat Recovery Data | same as above
i. | Filtration Data | same as above
j. | Humidifier Data | same as above
D. | Calculations:
1 | The external static pressure (ESP) calculation shall be submitted for each AHU system at the time of material submittal approval. | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
2 | External static pressure calculations based on approved installation drawings taking into account the actual resistance of the Air Handling Unit components and all duct fittings (including grilles, sound attenuators etc.) as provided by the manufacturers of such items for approval by the CA before final selection of units. | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
3 | Fan resistances shall take account of the pressure drop across filters in a dirty condition. | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
E. | Test Reports:
1 | AHU’s shall be factory tested for operation prior to shipment. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided at extra cost if required 3. Quality Control report will be provided during the time of delivery.
2 | Submit factory test reports and certificates of all factory quality control programmes | Comply | Quality Control reports will be provided during the time of delivery
3 | Provide list of tests included. | Comply | Quality Control reports will be provided during the time of delivery
4 | Provide copies of the certified test data. | Comply | Test copies would be provided during the time of delivery
F. | Installation Instructions:
1 | Submit manufacturer's installation instructions and installation method statement. | Comply | IOM manuals are provided
G. | Maintenance Data:
1 | Submit maintenance instructions, including instructions for lubrication, filter replacement, motor and drive replacement, and spare parts lists. Include this data, product data, shop drawings, and wiring diagrams in maintenance manuals. | In Contractor's scope | Please refer IOM manual for motor wiring
H. | Seismic Qualification Certificates (if seismic criteria apply to project):
1 | Provide the following for AHU’s, accessories and components from the manufacturer. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
a. | Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
b. | Dimensioned Outline Drawings of Equipment Unit: Identify centre of gravity and locate and describe mounting and anchorage provisions. | In Contractor's scope | AHU dimension shall be mentioned on datasheet
c. | Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. | In Contractor's scope | Daikin's responsibility is limited to manufacturing and delivering the AHUs to site (without unloading)
I. | Supplementary Product Literature:
1 | Include a statement from the manufacturer for the design life of the AHU components. | In Contractor's scope
J. | Submit a summary of deviations from the contract documents (if any). | In Contractor's scope
K. | Submit details of the manufacturers Quality Plan. | In Contractor's scope
3.3.2 | CLOSEOUT SUBMITTALS
A. | Comply with the requirements of Section 230010 Execution and Closeout Requirement and as stated elsewhere and submit the following: | In Contractor's scope
1 | Warranties as stated elsewhere | Noted | Product warranty shall be mentioned in DAIKIN AHU quotation
2 | Operation and Maintenance (O+M) Manuals:
a. | Include component list with manufacturer's reference numbers, descriptions of materials and procedures for repairing and cleaning of finishes and cleaning frequency. | Noted | IOM manuals are provided
b. | Include recommendations for unit maintenance. | Noted | IOM manuals are provided
c. | Include instructions for lubrication, filter replacement, motor and drive replacement, belt tension adjustments, wiring diagrams, and preventive/ routine maintenance check list. | Noted | IOM manuals are provided
3 | As-built Manufacturers Certified Drawings shall indicate the information detailed above. | Noted | AHU datasheet showing unit dimensions and weights are provided
4 | Provide spare parts as detailed elsewhere | Noted | Spare parts list will be update after completion the work, Spare parts can ordered with extra cost upon request
5 | Provide a complete set of spare filters for all AHUs as specified in Section 234100 HVAC Particulate Air Filters. | Noted | Spare parts list will be update after completion the work, Spare parts can ordered with extra cost upon request
3.2 | SUBMITTALS
A. | Product Data: Include rated capacities, operating characteristics, furnished specialties, and accessories. | Noted | AHU datasheet including all relevant data is provided
B. | LEED Compliance Submittals:
1 | Product Data for Credit EA 4: Documentation required by Credit EA 4 indicating that equipment and refrigerants comply. | In Contractor's scope | AHU dimension shall be mentioned on datasheet
2 | Product Data for Prerequisite EQ 1: Documentation indicating that units comply with ASHRAE 62.1-2010, Section 5 - "Systems and Equipment." | Noted | AHUs are selected as per scheduled data and datasheet including all relevant data is provided
C. | Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection. | In Contractor's scope | GA drawings shall be provided for AHUs during finalization.
1 | Wiring Diagrams: Power, signal, and control wiring. | In Contractor's scope | Please refer IOM manual for motor wiring
D. | Static Pressure calculations, electrical wiring diagram and the type of Control Panel Enclosure shall be included in the submittal. | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
E. | Coordination Drawings: Floor plans, reflected ceiling plans, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved: | In Contractor's scope | IOM manuals are provided
1 | Ceiling suspension components. | same as above
2 | Structural members to which fan-coil units will be attached. | same as above
3 | Method of attaching hangers to building structure. | same as above
4 | Size and location of initial access modules for acoustical tile. | same as above
5 | Items penetrating finished ceiling, including the following: | same as above
a. | Lighting fixtures. | same as above
b. | Air outlets and inlets. | same as above
c. | Speakers. | same as above
d. | Sprinklers. | same as above
e. | Access panels. | same as above
6 | Perimeter moldings for exposed or partially exposed cabinets. | same as above
F. | Samples for Initial Selection: For units with factory-applied color finishes. | In Contractor's scope | No sample shall be provided for AHUs
3.4 | SUBMISSIONS
A. | The Contractor shall calculate the external static pressure for the each air handling unit supply fan and exhaust/return air fan after finalizing the shop drawings, and prior to selecting the air handling units. The calculations shall be submitted and approved prior to the issue of the air handling unit material submittals. | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
B. | Submit the following information, where applicable, to the Engineer for approval in accordance with the requirements of this specification: | Noted
1 | Schedule of starting and full load currents | In Contractor's scope | AHU electric load shall be mentioned on datasheet
2 | Details of connections for fans | In Contractor's scope | AHU IOM manuals are provided for electrical connections
3 | Fan characteristic curves with operating point indicated | Comply | Fan curves are shown on AHU datasheet
4 | Sound pressure spectrums | Comply | Fan/Motor sound data provided in the AHU datasheet based on measurements taken in a free field environment and spherical propagation
5 | Vibration mounting details, including isolation efficiency on high and low speed | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
6 | Coil pressure drops, air side and water side | Comply | Coil data is provided in AHU datasheet
7 | Coil air on and air off conditions | Comply | Coil data is provided in AHU datasheet
8 | Coil water on and water off temperatures | Comply | Coil data is provided in AHU datasheet
9 | Fan motor rating and design absorbed power | Comply | Fan Motor data is provided in AHU datasheet
10 | Fan and motor speeds | Comply | Fan Motor data is provided in AHU datasheet
11 | Drive belt sizes | Comply with Remarks | Drive sizes can be provided at the time of delivery
12 | Filter sizes and efficiencies | Comply | Filter details and sizes are provided in AHU datasheet
13 | Fan static and total pressures | Comply | Fan data is provided in AHU datasheet
14 | External to unit, static and total pressures | In Contractor's scope | Fans are selected based on the scheduled external pressure drop, while internal pressure drops for all components are specified in AHU datasheet
15 | Humidifier model and rating | Comply | AHU datasheet includes all relevant data required for various components
16 | Attenuator insertion losses | Comply | AHU datasheet includes all relevant data required for various components
17 | Electric heater model and rating | Comply | AHU datasheet includes all relevant data required for various components
18 | Heat pipe selection details | Comply | AHU datasheet includes all relevant data required for various components
19 | Heat Recovery selection details | Comply | AHU datasheet includes all relevant data required for various components
C. | Fully dimensioned manufacturing drawings shall be submitted to the Engineer of all units for approval prior to manufacture. | In Contractor's scope | GA drawings shall be provided for AHUs during finalization.
3.5 | SUBMITTALS
A. | Product Data for each central-station air-handling unit specified, including the following: | Noted
1 | Submittals for AHUs shall include fans, drives, motors, coils, humidifiers, sound attenuators, mixing box with outside/return air dampers, filter housings, and all other related accessories. | Comply with Remarks | DAIKIN shall submit all technical product datasheets for all AHU components, including unit construction, dimensions, weights, performance. IOM manual shall be provided for maintenance requirements.
2 | The Contractor shall provide custom drawings showing total air-handling unit assembly including dimensions, access sections, diffusion plates, flexible connections, door swings, control penetrations, electrical disconnect, lights, duplex outlets, switches, wiring, utility connection points, unit support system, vibration isolators, drain pan, and rigging points. Submittal drawings of section or component only, will not be acceptable. The Contractor shall also submit performance data including performance test results, charts, curves or certified computer selection data; data sheets; fabrication and insulation details; and the number of pieces that each unit will have to be broken into to meet shipping and job site rigging requirements. | Comply with Remarks | DAIKIN shall submit all technical product datasheets for all AHU components, including unit construction, dimensions, weights, performance. IOM manual shall be provided for maintenance requirements.
3 | Submit certified fan-sound power ratings showing sound power levels in each octave band for fan and at entrance and discharge of AHUs at both present and future scheduled conditions. Include sound attenuator capacities and itemized internal component attenuation. Internal lining of supply air ductwork with sound absorbing material is not permitted. | In Contractor's scope | Fan/Motor sound data provided in the AHU datasheet based on measurements taken in a free field environment and spherical propagation. Units don't have sound attenuators. Duct sound attenuators shall be in scope of contractor.
4 | Provide certified fan curves showing cubic meters per minute (cubic feet per minute), static pressure, efficiency, and horsepower for both present and future design point of operation and at maximum of present and future design cubic meters per minute (cubic feet per minute) and 110 percent of design static pressure. | Comply with Remarks | AHUs are selected at scheduled data. Fan data is provided in AHU datasheet
5 | Submit total fan static pressure, external static pressure, for AHU including total, inlet and discharge pressures, and itemized specified internal losses and unspecified internal losses. Refer to air-handling unit schedule on drawings. | Comply | AHUs are selected at scheduled data. Fan data is provided in AHU datasheet
6 | Certified coil-performance ratings with system operating conditions indicated. | Comply | Coil data is provided in AHU datasheet
7 | Motor ratings and electrical characteristics plus motor and fan accessories. | Comply | Fan Motor data is provided in AHU datasheet
8 | Material gages and finishes. | Comply | Technical product datasheet shall contain necessary details for individual AHUs
9 | Filters with performance characteristics. | Comply | Filter details and sizes are provided in AHU datasheet
10 | Dampers, including housings, linkages, and operators. | In Contractor's scope | Damper details are provided in AHU datasheet.
B. | LEED Submittals:
1. | Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment." | Noted | AHUs are selected as per scheduled data and datasheet including all relevant data is provided
C. | Delegated-Design Submittal: For vibration isolation[ and seismic restraints] indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
1 | Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting. | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
2 | Design Calculations: Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases. | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
D. | Shop Drawings from manufacturer detailing equipment assemblies and indicating dimensions, weights, loadings, required clearances, method of field assembly, components, and location and size of each field connection. | In Contractor's scope | GA drawings shall be provided for AHUs during finalization.
E. | Wiring diagrams detailing wiring for power and control systems and differentiating between manufacturer-installed and field-installed wiring. | In Contractor's scope | Please refer IOM manual for motor wiring
F. | Coordination Drawings, including floor plans and sections drawn to scale. Submit with Shop Drawings. Show mechanical-room layout and relationships between components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate and certify field measurements. | In Contractor's scope | IOM manuals are provided
G. | Seismic Qualification Certificates: For air-handling units, accessories, and components, from manufacturer. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
1 | Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation. | In Contractor's scope | Seismic requirements to be provided by contractor. Compliance statement is provided for Air Handling units only.
2 | Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. | In Contractor's scope | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed. It is not necessary to place anti-vibration material between the unit and the floor: the moving parts are dynamically isolated from the structure.
3 | Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. | In Contractor's scope | Daikin's responsibility is limited to manufacturing and delivering the AHUs to site (without unloading)
H. | Field Commissioning Reports: As specified in "Commissioning" Article in Part 3 of this Section. Indicate and interpret test results for compliance with performance requirements. | In Contractor's scope | Daikin's responsibility is limited to manufacturing and delivering the AHUs to site (without unloading)
I. | Operation and Maintenance data for central-station air-handling units to include in the operation and maintenance manual specified in Division 1. | Comply | IOM manuals are provided
1. | Include: Lists of parts and troubleshooting maintenance data. | Comply | IOM manuals are provided
J. | Warranties: Warranties specified in this Section. | Noted | Product warranty shall be mentioned in DAIKIN AHU quotation
3.6 | SUBMITTALS
A. | Product Data: For each air-handling unit indicated. | Comply | Technical product datasheet shall contain necessary details for individual AHUs
1 | Unit dimensions and weight. | Comply | Technical product datasheet shall contain necessary details for individual AHUs
2 | Cabinet material, metal thickness, finishes, insulation, and accessories. | Comply | Technical product datasheet shall contain necessary details for individual AHUs
3 | Fans:
a. | Certified fan-performance curves with system operating conditions indicated. | Comply | Fan curves are shown on AHU datasheet
b. | Certified fan-sound power ratings. | Comply | Fan Motor data is provided in AHU datasheet
c. | Fan construction and accessories. | Comply | Fan catalogue can be provided
d. | Motor ratings, electrical characteristics, and motor accessories. | Comply | Fan Motor data is provided in AHU datasheet
4 | Certified coil-performance ratings with system operating conditions indicated. | Comply | Coil data is provided in AHU datasheet
5 | Dampers, including housings, linkages, and operators. | In Contractor's scope | Damper details are provided in AHU datasheet.
6 | Filters with performance characteristics. | Comply | Filter details and sizes are provided in AHU datasheet
B. | Coordination Drawings: Floor plans and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved: | In Contractor's scope | GA drawings shall be provided for AHUs during finalization.
1 | Mechanical-room layout and relationships between components and adjacent structural and mechanical elements. | same as above
2 | Support location, type, and weight. | same as above
3 | Field measurements. | same as above
C. | Source quality-control reports. | same as above
D. | Field quality-control reports. | same as above
E. | Operation and Maintenance Data: For air-handling units to include in emergency, operation, and maintenance manuals. | In Contractor's Scope | IOM manuals are provided
3.7 | SUBMITTALS
B. | Product Data:
| Published Literature: Indicate dimensions, weights, capacities, ratings, gages and finishes of materials, and electrical characteristics and connection requirements. | In contractor's Scope | AHU Datasheets are provided by the manufacturer
| Filters: Data for filter media, filter performance data, filter assembly, and filter frames. | In contractor's Scope | AHU Datasheets are provided by the manufacturer
| Fans: Performance and fan curves with specified operating point clearly plotted, power, RPM. | In contractor's Scope | AHU Datasheets are provided by the manufacturer
| Sound Power Level Data: Fan outlet and casing radiation at rated capacity. | In Contractor's Scope | AHU Datasheets are provided by the manufacturer
| Electrical Requirements: Power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring. | In Contractor's Scope | AHU Datasheets are provided by the manufacturer
C. | Shop Drawings: Indicate assembly, unit dimensions, weight loading, required clearances, construction details, field connection details, and electrical characteristics and connection requirements. | In Contractor's Scope | IOM manuals are provided
D. | Manufacturer's Instructions: Include installation instructions. | In Contractor's Scope | IOM manuals are provided
E. | Maintenance Data: Include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists, and wiring diagrams. | In Contractor's Scope | IOM manuals are provided
A. | Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience. | Comply
B. | Manufacturer to certify his products for outdoor installation and capable of withstanding sea ambient conditions without corrosion and possible damage. | In Contractor's Scope | AHUs are selected as per scheduled data and provided specifications
C. | Units shall be listed and bear the label of the Air Conditioning and Refrigeration Institute (AHRI 430). | Comply | DAIKIN AHUs are EUROVENT certified, Cooling coils are AHRI certified
D. | Condensation: During first year guarantee period, if condensation forms on any section of air handler when unit is operating at design conditions, the Contractor shall replace or repair unit to correct the situation. Repairs shall not impair unit or component accessibility and future reparability and inherent access for maintenance. All repairs shall be subject to the Engineer’s approval. | In Contractor's Scope | To avoid condensation Thermal Break units can be provided
3.8 | ADMINISTRATIVE REQUIREMENTS
A. | Coordination: Coordinate the installation of the unit with size, location and installation of service utilities.
B. | Coordinate the work with other trades for installation of roof mounted air handling units on roof curbs.
C. | Preinstallation Meeting: Conduct a preinstallation meeting one week prior to the start of the work of this section; require attendance by all affected installers.
D. | Sequencing: Ensure that utility connections are achieved in an orderly and expeditious manner.
3.9 | SUBMITTALS
A. | See Section 01 30 00 - Administrative Requirements for submittal procedures.
B. | Product Data:
1. | Published Literature: Indicate dimensions, weights, capacities, ratings, gauges and finishes of materials, and electrical characteristics and connection requirements.
2. | Filters: Data for filter media, filter performance data, filter assembly, and filter frames.
3. | Fans: Performance and fan curves with specified operating point clearly plotted, power, RPM.
4. | Sound Power Level Data: Fan outlet and casing radiation at rated capacity.
5. | Electrical Requirements: Power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.
C. | Sustainable Design Documentation: Submit manufacturer's product data on refrigerant used, showing compliance with specified requirements.
D. | Shop Drawings: Indicate assembly, unit dimensions, weight loading, required clearances, construction details, field connection details, and electrical characteristics and connection requirements.
E. | Samples: Submit two of each type of replacement filter media with frame.
F. | Specimen Warranty: Submit sample of manufacturer's warranty.
G. | Executed Warranty: Submit documentation of final executed warranty completed in Owner's name and registered with manufacturer.
H. | Manufacturer's Instructions: Include installation instructions.
I. | Maintenance Data: Include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists, and wiring diagrams.
J. | Maintenance Materials: Furnish the following for Owner's use in maintenance of project.
1. | See Section 01 60 00 - Product Requirements for additional provisions.
2. | Extra Fan Belts: One set for each unit.
3. | Extra Filters: One set for each unit.

## 4. Quality Assurance
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
4.1 | QUALITY ASSURANCE
A. | All Air Handling Units shall be sourced from a single manufacturer. | Comply | DAIKIN AHUs are supplied
B. | The manufacturer shall have a minimum 10 years’ experience in the design and manufacture of AHU’s. The manufacturing facilities shall be fully accredited to the highest quality management standards, certified to ISO 9001 and 14001. | Comply | DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility
C. | The manufacturer shall have a committed customer care and technical support team, complimented by a dedicated service team providing a call out service within the country the AHU’s are installed. | Comply | DAIKIN shall provide customer care support and service support.
D. | Standards and other Codes of Practice: In addition to the requirements indicated on the Drawings or in the Specification, the Works shall be in accordance with provisions of the following standards and codes. The current editions of the publications listed below form a part of this Section. | Noted
1 | BSI Group, (BS) British Standards, including;
a. | BS EN 1886 – Air Handling Units – Mechanical performance | Comply | DAIKIN AHUs are Eurovent certified
b. | BS EN 13053 – Air Handling Units – Ratings and Performance | Comply | DAIKIN AHUs are Eurovent certified
2 | Underwriters' Laboratories, UL Standards.
3 | Factory Mutual System, FM Standards.
4 | National Fire Protection Association, NFPA Standards:
a. | NFPA 90A Standard for the Installation of Air-Conditioning and Ventilating Systems. | Noted | Foam insulation Surface spread of flame class 1 as per ASTM 84 (FSI <25 & SDI<250), Fire resistance class 1 as per BS 476 part 6&7. | NFPA 90A Section 4.3.3 Requirements * Maximum Flame Spread Index: 25 * No Continued Progressive Combustion * Maximum Smoke Developed Index: 50 🔍 Note: The fire performance criteria outlined in NFPA 90A are significantly more stringent than those of a Class A fire rating. While both standards require a maximum flame spread index of 25, NFPA 90A limits the smoke developed index to 50, compared to 450 allowed under Class A.
5 | International Code Council, ICC Standards: | Noted
a. | International Building Code, IBC. | Noted
b. | International Mechanical Code, IMC. | Noted
6 | All Air handling Units shall be Eurovent Certified | Comply | DAIKIN AHUs are Eurovent certified
7 | American Water Works Association, AWWA Standards. | Noted
8 | American Society of Mechanical Engineers, ASME Standards. | Noted
9 | International Organization for Standardization, ISO Standards. | Comply | DAIKIN AHUs are manufactured in an ISO certified facility
10 | American Standards Association, ASA Standards. | Noted
11 | American National Standards Institute, ANSI Standards. | Noted
12 | Air-Conditioning and Refrigeration Institute, ARI Standards:
13 | ARI 410 Standard for Forced-Circulation Air-Cooling and Air-Heating Coils. International Electrotechnical Commission, IEC Standards. | Comply | DAIKIN AHUs shall be with AHRI certified coils. Motors shall comply with IEC standards.
E. | Electrical Components, Devices, and Accessories:
1 | Listed and labelled as defined in IEC by a testing agency acceptable to the Municipality and Utility Authority having jurisdiction, and marked for intended use. | Comply | DAIKIN AHU motors shall comply with IEC standards. | AC Motors: Electric codes are as per IEC standard & motor comply with IEC-60034-1.
F. | Preconstruction Testing/ Reports
1 | Submit reports of independent tests demonstrating that the products and systems comply with the specified performance requirements. | In Contractor's scope | Daikin shall provide AHU Datasheets and after manufacturing QC reports shall be provided
2 | Where test results for a material or product are not available, undertake testing to show compliance with the Specification at an independent testing laboratory acceptable to the CA at no additional cost. | In Contractor's scope
3 | The provision of testing data or the carrying-out of tests does not relieve the Contractor of his responsibilities regarding the performance requirements, durability or service life requirements. | In Contractor's scope
4 | National Fire Protection Association, NFPA Standards:
a. | NFPA 90A Standard for the Installation of Air-Conditioning and Ventilating Systems. | Noted | Foam insulation Surface spread of flame class 1 as per ASTM 84 (FSI <25 & SDI<250), Fire resistance class 1 as per BS 476 part 6&7. | NFPA 90A Section 4.3.3 Requirements * Maximum Flame Spread Index: 25 * No Continued Progressive Combustion * Maximum Smoke Developed Index: 50 🔍 Note: The fire performance criteria outlined in NFPA 90A are significantly more stringent than those of a Class A fire rating. While both standards require a maximum flame spread index of 25, NFPA 90A limits the smoke developed index to 50, compared to 450 allowed under Class A.
5 | All tests shall be carried out in accordance with the relevant British Standard or equivalent international standard. | Noted
G. | All materials supplied and installed shall be new and the best quality obtained for the intended purpose and shall, where applicable, conform to the standards of and shall be approved from Local By-laws and Regulations. | Noted
H. | All materials required for installation under these specifications shall be subject to the acceptance of the CA. Where no specific indication as to the type or quality of material or equipment is indicated, a first class standard article to the CA's acceptance shall be provided. | Noted
4.2 | QUALITY ASSURANCE
A. | Electrical Components, Devices, and Accessories: Listed and labelled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use. | Noted | Foam insulation Surface spread of flame class 1 as per ASTM 84 (FSI <25 & SDI<250), Fire resistance class 1 as per BS 476 part 6&7.
B. | ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Start-up." | In Contractor's scope
C. | ASHRAE/IESNA 90.1-2010 Compliance: Applicable requirements in ASHRAE/IESNA 90.1-2010, Section 6 - "Heating, Ventilating, and Air-Conditioning." | Noted
D. | Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." | Noted |  | EC Fans: Offered units Motors are IE4 with EC fans in accordance with European standards Ecodesign EU regulation EU 327/2011. Motors are in accordance with IEC standards and IE3 rated (equivalent to NEMA MG-1).
E. | Unit manufacturers shall have ISO 9001: 2018 certification for Quality Management Systems. | Comply |  | DAIKIN have ISO 9001, ISO 14001, ISO 45001 certification
F. | ISO 14001: 2018 certification for Environmental Management Systems | Comply |  | DAIKIN have ISO 9001, ISO 14001, ISO 45001 certification
G. | OHSAS 45001:2018 certification for Occupational Health and Safety | Comply |  | DAIKIN have ISO 9001, ISO 14001, ISO 45001 certification
H. | Eurovent certification | Comply |  | EUROVENT Compliance: Design, Test, and rate air handling units in accordance with Eurovent Standard EN1886 & EN13053, display certification symbol on units of certified models.
I. | Manufacturer / manufacturer’s representative should carry enough stock of spares including fans, motors, etc., locally to minimize breakdown response time. | Comply with Remarks | DAIKIN engineer can be provided (at extra cost)
4.3 | QUALITY ASSURANCE
A. | NFPA Compliance: Central-station air-handling units and components shall be designed, fabricated, and installed in compliance with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems." | Noted | Foam insulation Surface spread of flame class 1 as per ASTM 84 (FSI <25 & SDI<250), Fire resistance class 1 as per BS 476 part 6&7. | NFPA 90A Section 4.3.3 Requirements * Maximum Flame Spread Index: 25 * No Continued Progressive Combustion * Maximum Smoke Developed Index: 50 🔍 Note: The fire performance criteria outlined in NFPA 90A are significantly more stringent than those of a Class A fire rating. While both standards require a maximum flame spread index of 25, NFPA 90A limits the smoke developed index to 50, compared to 450 allowed under Class 1.
C. | Manufacturers of air handling units shall have ISO 9002 Certification. | Comply |  | DAIKIN have ISO 9001, ISO 14001, ISO 45001 certification
D. | The Air Handling Unit and all internal components such as “Coils, Fans and Filters etc” should be manufactured to ISO 9002 (BS 5750 part 1) Quality Assurance standards and ISO 14001 Environmental Standards. | Comply |  | DAIKIN have ISO 9001, ISO 14001, ISO 45001 certification
E. | The Air Handling supplier should supply the first line product, which should be Eurovent Certified. The Eurovent certificate should show the product model, range, factory name and Country of origin. | Comply | DAIKIN AHUs are Eurovent certified
F. | Electrical components required as part of air handling units, shall be listed and labeled by UL and comply with IEE Standards. | Comply | DAIKIN AHU motors shall comply with IEC standards. | Electric codes are as per IEC standard & motor comply with IEC-60034-1
J. | Air handling unit fan performance, sound rating, coil performance and lubrication should be as per EN 13053/ARI 430. | Comply | DAIKIN AHUs are Eurovent certified
4.4 | QUALITY ASSURANCE
A. | Equipment shall demonstrate compliance with requirements specified in Section | Noted
B. | Comply with the applicable requirements and recommendations of local Saudi Building Code (SBC) and the latest applicable local regulations for materials, tests, installation, and identification for air-handling units, as listed in, but not - whichever is more stringent. | Noted
C. | NFPA Compliance: Central-station air-handling units and components shall be designed, fabricated, and installed in compliance with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems." | Noted | Foam insulation Surface spread of flame class 1 as per ASTM 84 (FSI <25 & SDI<250), Fire resistance class 1 as per BS 476 part 6&7. | NFPA 90A Section 4.3.3 Requirements * Maximum Flame Spread Index: 25 * No Continued Progressive Combustion * Maximum Smoke Developed Index: 50 🔍 Note: The fire performance criteria outlined in NFPA 90A are significantly more stringent than those of a Class A fire rating. While both standards require a maximum flame spread index of 25, NFPA 90A limits the smoke developed index to 50, compared to 450 allowed under Class 1.
D. | UL/ETL Compliance: Electric coils, along with complete central-station airhandling unit, shall be listed and labeled by ETL in compliance with UL requirements. | Noted
E. | AHRI Certification: Central-station air-handling units and their components shall be factory tested according to the applicable portions of ANSI/AHRI 430, "Performance Rating of Central-Station Air-Handling Units," and shall be listed and bear the label of the Air-Conditioning, Heating and Refrigeration Institute (AHRI) or equivalent relevant BS/EN standards. | Comply | DAIKIN AHUs shall be with AHRI certified coils.
F. | Provide motors required as part of air-handling units that are listed and labeled by UL and comply with applicable NEMA standards or equivalent characteristics in accordance with applicable parts of IEC 60034. | Comply | DAIKIN AHU motors shall comply with IEC standards. | Electric codes are as per IEC standard & motor comply with IEC-60034-1
G. | Condensation: During first year guarantee period, if condensation forms on any section of air handler when unit is operating at design conditions, the Contractor shall replace or repair unit to correct the situation. Repairs shall not impair unit or component accessibility and future reparability and inherent access for maintenance. | Comply |  | Our units have TB2 class as per Eurovent.
H. | Electrical Components, Devices, and Accessories: Listed and labeled as defined in latest and relevant IEC standard, by a testing agency acceptable to the Engineer. | Comply | DAIKIN AHU motors shall comply with IEC standards. | Electric codes are as per IEC standard & motor comply with IEC-60034-1
I. | Listing and Labeling: Provide electrically operated components specified in this Section that are listed and labeled. | Noted
4.5 | QUALITY ASSURANCE
A. | Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application. | Noted
B. | NFPA Compliance: Comply with NFPA 90A for design, fabrication, and installation of air-handling units and components. | Noted | Foam insulation Surface spread of flame class 1 as per ASTM 84 (FSI <25 & SDI<250), Fire resistance class 1 as per BS 476 part 6&7. | NFPA 90A Section 4.3.3 Requirements * Maximum Flame Spread Index: 25 * No Continued Progressive Combustion * Maximum Smoke Developed Index: 50 🔍 Note: The fire performance criteria outlined in NFPA 90A are significantly more stringent than those of a Class A fire rating. While both standards require a maximum flame spread index of 25, NFPA 90A limits the smoke developed index to 50, compared to 450 allowed under Class 1.
C. | AHRI Certification: Air-handling units and their components shall be factory tested according to AHRI 430, "Central-Station Air-Handling Units," and shall be listed and labeled by AHRI. | Comply | DAIKIN AHUs are with AHRI certified coils
D. | ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section of Systems and Equipment and Section of “Construction and Startup." | In Contractor's scope
E. | Comply with NFPA 70. | Noted
4.6 | TESTING
| AHRI certified AHUs: No individual testing of each required. | Comply | DAIKIN AHUs are with AHRI certified coils
| Non-AHRI certified AHUs: All units shall be factory assembled and tested. | Noted
| Units specified to be tested shall be factory assembled and tested in accordance with specified Test Procedure to demonstrate compliance with required unit capacities, ensure correct fit of all components and minimize field assembly labor. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided at extra cost if required 3. Quality Control report will be provided during the time of delivery. | Unit shall be manufactured, rated, tested and certified in accordance with EN13053 and EN1886.
B. | Factory Test: One AHU chosen by the engineer shall be factory tested for Casing leakage test at the maximum working fan pressure. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided at extra cost if required 3. Quality Control report will be provided during the time of delivery. | Remove FAT if price not considered in quotation
| Air volume, static pressure for AHU and each component, fan RPM and power consumption for the maximum of present or future design conditions. Submit fan curves showing test results. | Comply | Fan curves are shown on AHU datasheet
C. | Approval:
| Factory tests shall be witnessed by the Engineer’s and Employer’s representative. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided at extra cost if required 3. Quality Control report will be provided during the time of delivery. | Remove FAT if price not considered in quotation
| Failure of AHU to meet test requirements shall require correction of deficiency and retesting of unit. | Noted
| Submit written results of factory tests for approval prior to shipping. | Noted
A. | Products Requiring Electrical Connection: Listed and classified by UL (DIR) as suitable for the purpose specified and indicated. | Comply | DAIKIN AHU motors shall comply with IEC standards. | Electric codes are as per IEC standard & motor comply with IEC-60034-1
4.7 | QUALITY ASSURANCE
A. | Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 5. Delivery, Storage And Hand
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
5.1 | DELIVERY, STORAGE AND HANDLING
A. | Units shall be shipped fully assembled (on factory installed base rails/ mounting legs) up to practical shipping and rigging limitations. Units not shipped fully assembled shall have labels and airflow arrows on each section to indicate location and orientation in direction of airflow. | Comply
B. | Each section shall have lifting lugs of shipping skid to allow for field rigging and final placement of section. | Comply | Every module or mono-block unit has lifting holes
C. | Deliver units to Site with fan motors, sheaves and belts completely assembled and mounted in units. | Comply
D. | Store in clean dry place and protect from weather and construction traffic. Handle carefully to avoid damage to components, enclosures and finish. | In Contractor's scope | Daikin's responsibility is limited to manufacturing and delivering the AHUs to site (without unloading)
E. | Unit shall be handled and stored in accordance with the manufacturer’s instructions. | In Contractor's scope | Daikin's responsibility is limited to manufacturing and delivering the AHUs to site (without unloading)
5.2 | DELIVERY, STORAGE, AND HANDLING
A. | Deliver air-handling unit as a factory-assembled module with protective crating and covering. | Comply | Units are nylon wrapped and delivered on wooden Crating. Lifting holes are provided on base frame for lifting the units | Units are nylon wrapped and delivered on wooden pieces on 4 corners. Lifting holes are provided on base frame for lifting the units. IOM Manual: The units are normally shipped with shrink-wrap packaging and divided into modules to be assembled at the installation site. All details necessary for assembly of the sections are placed, adequately protected, inside one of the sections of the unit.
B. | Lift and support units with manufacturer's designated lifting or supporting points. | Comply | Lifting holes are provided on base frame for lifting the units
5.2.2 | SEQUENCING AND SCHEDULING
A. | Coordinate size and location of concrete housekeeping bases. Cast anchor-bolt inserts into base. | In Contractor's scope
B. | Coordinate size and location of structural-steel support members. | In Contractor's scope
5.3 | COORDINATION
A. | Coordinate sizes and locations of concrete bases with actual equipment provided. | In Contractor's scope |  | It is recommended to use rubber isolation pads between the AHUs base frame and the plinth/base structure on which the AHUs are placed
B. | Coordinate sizes and locations of structural-steel support members, if any, with actual equipment provided. | In Contractor's scope
5.4 | DELIVERY, STORAGE, AND HANDLING
A. | Accept products on site in factory-fabricated protective containers, with factory-installed shipping skids and lifting lugs. Inspect for damage. | In contractor's Scope | IOM manuals are provided
B. | Store in clean dry place and protect from weather and construction traffic. Handle carefully to avoid damage to components, enclosures, and finish. | In contractor's Scope | IOM manuals are provided
C. | Do not operate units until ductwork is clean, filters are in place, bearings lubricated, and fan has been test run under observation. | In contractor's Scope | IOM manuals are provided

## 6. Warranty and Others
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
6.1 | WARRANTY:
A. | Air handling units shall be provided with a warranty as detailed in Division 230010. | Noted
6.1.2 | PROJECT CONDITIONS
A. | Do not operate units for any purpose, temporary or permanent, until ductwork is clean, filters are in place, bearings lubricated and fan has been test run under observation. | In Contractor's scope
6.2 | WARRANTY
A. | Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of condensing units those fail in materials or workmanship within specified warranty period. | Noted
1 | Failures include, but are not limited to, the following: | Noted
a. | Electric motor failure. | Noted
b. | Chilled Water Coil leak. | Noted
2 | Warranty Period: 2 years from date of Take Over. | Comply with Remarks | Standard AHU warranty shall be 12 months from date of startup or 18 months from the delivery date, whichever occurs first
6.3 | WARRANTY
A. | Manufacturer's Warranty: Provide written warranty, signed by manufacturer agreeing to repair or replace components of the modular central-station airhandling units that fail in materials or workmanship within specified warranty period. | Comply with Remarks | Standard AHU warranty shall be 12 months from date of startup or 18 months from the delivery date, whichever occurs first
B. | Warranty Period: Two years from date of Substantial Completion. | Comply with Remarks | Standard AHU warranty shall be 12 months from date of startup or 18 months from the delivery date, whichever occurs first
6.4 | WARRANTY
A. | Refer to Division 01 Section "PROJECT CLOSEOUT / SUBSTANTIAL COMPLETION PROCEDURES" for additional warranty requirements.
B. | Provide a minimum of three(3) years warranty for product(s) and/or equipment under this section. This includes coverage for complete equipment as manufactured and delivered to site including materials and labor from the date of Substantial Completion (Practical Completion) and handover of project.

## 7. Spare Parts
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 1 - GENERAL
7.1 | EXTRA MATERIALS
A. | Furnish extra materials described below that match products installed, are packaged with protective covering for storage, and are identified with labels describing contents. | Noted
B. | Filters: Furnish 1 set for each central-station air-handling unit. | Complied with extra cost | Required set of spare parts can be provided
C. | Fan Belts: Furnish 1 set for each central-station air-handling unit fan. | Complied with extra cost | Required set of spare parts can be provided
D. | Gaskets: Furnish 1 set for each sectional joint of each central-station air-handling unit. | Complied with extra cost | Required set of spare parts can be provided

## 8. General Requirements
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
8.1 | GENERAL REQUIREMENTS
A. | This Section includes the requirements for the design, construction and installation of air handling units and components. | Noted
B. | All AHU’s shall be designed and tested in accordance with BS EN 1886 and BS EN 13053. | Comply | DAIKIN AHUs are Eurovent certified | Eurovent Ratings
C. | The AHU assembly and construction of panels to the frames shall provide minimum air leakage Class-A according to EUROVENT Standard 2/2. | Comply | DAIKIN AHUs shall be with L1(M) casing leakage class in accordance with Eurovent EN1886 | Eurovent Ratings
D. | The duties and performance of the units shall be in accordance with the details indicated elsewhere and include any allowance required to meet manufacturing tolerances. | Comply | Duties and performance of the DAIKIN AHUs shall be in accordance with the specifications and requirements detailed in the Schedule/Tender documents
E. | Individual components shall, in addition to the requirements of this section, comply with other relevant sections of this specification. | Comply | Duties and performance of the DAIKIN AHUs shall be in accordance with the specifications and requirements detailed in the Schedule/Tender documents
F. | Air handling units shall be fully assembled and tested at the manufacturer’s works to demonstrate that aerodynamic performance, leakage air flow, design resistance and noise levels are in compliance with the specification and performance requirements. The results and a compliance statement shall be submitted to the CA prior to delivery to site. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided at extra cost if required 3. Quality Control report will be provided during the time of delivery. | Unit shall be manufactured, rated, tested and certified in accordance with EN13053 and EN1886. Remove FAT if price not considered in quotation
G. | Where units are delivered to site disassembled, the manufacturer shall allow for the site erection of the units. | Assembly in Contractor's scope | DAIKIN engineer can be provided to supervise the installation (at extra cost)
H. | The manufacturer shall undertake a pre-commission check to ensure suitability for dynamic commissioning and a report shall be issued to the CA. | Comply with Remarks | 1. DAIKIN AHUs are Eurovent certified and are manufactured in an ISO certified facility. 2. Factory Acceptance Test can be provided at extra cost if required 3. Quality Control report will be provided during the time of delivery. | Unit shall be manufactured, rated, tested and certified in accordance with EN13053 and EN1886. Remove FAT if price not considered in quotation
I. | Units and their components shall incorporate lifting facilities for installation. | Comply | Every module or mono-block unit has lifting holes
J. | Units shall be draw-through type, unless specifically required as blow-through units. | Noted
K. | Fresh air and exhaust connections shall be provided with tight shut-off dampers arranged to close when the system shuts down unless otherwise stated. | Noted
L. | All necessary penetrations in the air handling unit casing e.g. to accommodate controls items etc., shall be undertaken at the factory. Penetrations shall not be permitted on site. | Comply | All necessary Tapping Points are provided as per inputs during manufacturing stage. | Factory can provide all necessary Penetrations marked by client during GA drawing approval
M. | Electrical work shall conform to IEC Standards and as stated elsewhere. | Comply | Unit Internal electrical works shall comply with IEC standards.
N. | Electrical characteristics of equipment shall be as detailed in the Equipment Schedules and Drawings and in accordance with the requirements of the Authority Having Jurisdiction. | Comply | Duties and performance of the DAIKIN AHUs shall be in accordance with the specifications and requirements detailed in the Schedule/Tender documents
8.2 | GENERAL REQUIREMENTS
1 | Each unit shall consist of fans, motors, V-belt drives, cooling-coil, heating element (when specified), drain pan, filters and necessary controls. | Comply | DAIKIN AHUs shall be in accordance with the specifications and requirements detailed in the Schedule/Tender documents
2 | The unit shall be mounted on a suitable base. In all cases approved vibration eliminators shall be provided. The Contractor shall submit details of bases, mountings and connections to the Engineer for approval. | Comply | Base frame shall be C-channel type and made of hot dipped Galvanized steel for all sizes | Base frame shall be C-channel type and made of hot dipped Galvanized steel for all sizes. Base frame made of Sendzimer GI, height 100mm, thickness 2.8 mm, C-channel type. Self drilling screws are used to fix the base frame with aluminum profile. Side & lateral support frames are bolted together.
3 | The unit(s) shall be of the draw thru Low/medium pressure type. | Noted
4 | If not shown elsewhere in Acoustic Specialist Report the measured sound transmission loss of the air handling units casing shall not be less than: | Comply | Please refer to selection report of AHUs for sound data. | Please refer to selection report of AHUs for sound data. If any sound reduction is required, it will be done at site by contrator
63 125 250 500 1K 2K 4K HZ dB
5 | The listed sound transmission loss is the minimum required sound reduction from the fan chamber to the plant room for an air handling unit that has supply and return ducted systems. | In Contractor's scope | If any sound reduction is required, it will be done at site by contrator
6 | The contractor shall confirm to the Engineer the total static pressure of the fan after the Engineer's approval on the air handler and after preparing the shop Drawings. | In Contractor's scope
7 | Units shall be suitable for variable air volume application where specified in capacity schedule. | Noted
8 | The Units shall be factory assembled. | Noted
8.3 | MANUFACTURERS
A. | Material and equipment shall be the standard products of a manufacturer regularly engaged in the manufacturing of such products, which are of a similar material, design and workmanship. The standard products shall have been in satisfactory commercial or industrial use for 5 years prior to bid opening. The 5 year use shall include applications of equipment and materials under similar circumstances and of similar size. However, digital electronics devices, software and systems such as controls, instruments, Operator interface devices, shall be the current generation of technology and basic design that has a proven satisfactory service record . The 5 years experience shall be satisfactorily completed by a product that has been sold or is offered for sale on the commercial market through advertisements, service record shall not be acceptable. | Comply
B. | Material shall be supported by a local service organization, authorized and trained by the mannufacturer of the equipment supplied. System components shall be enviromentally suitable for the indicated locations. | Comply
8.3.1 | GENERAL
A. | AHUs shall be entirely of double wall galvanized steel construction. Galvanizing shall be hot dipped conforming to A653/A653M and shall provide a minimum of 0.275 kg of zinc per square meter (0.90 oz. of zinc per square foot) (G90). | Comply |  | Unit casing is made of GI which is coated in accordance with ASTM A653. G90 is a coating thickness designation in the galvanizing specification ASTM A653. This specification is for hot-dip galvanizing steel sheet using the continuous (high-speed) galvanizing process.
| and documentation that structural rigidity is equal or greater than the galvanized steel specified. | Noted
B. | General Description: Factory assembled, consisting of fans, motor and drive assembly, coils, damper, plenums, filters, drip pans, mixing dampers, and discharge collars with flexible duct connectors. | Noted
C. | The Contractor and the AHU manufacturer shall be responsible for insuring that the unit will not exceed the allocated space shown on the drawings, including required clearances for service and future overhaul or removal of unit components. | In Contractor's scope | AHU dimension shall be mentioned on datasheet
| All structural, piping, wiring, and ductwork alterations of units, which are dimensionally different than those specified, shall be the responsibility of the Contractor at no additional cost to the Employer. | In Contractor's scope
D. | AHUs shall be fully assembled by the manufacturer in the factory in accordance with the arrangement shown on the drawings. | Comply
| The unit shall be assembled into the largest sections possible subject to shipping and rigging restrictions. | Comply | Units shall be shipped disassembled to the minimum module size in accordance with jobsite requirements for ease of rigging and installation. | The units are normally shipped with shrink-wrap packaging and divided into modules to be assembled at the installation site. All details necessary for assembly of the sections are placed, adequately protected, inside one of the sections of the unit.
| The correct fit of all components and casing sections shall be verified in the factory for all units prior to shipment. | Comply
| Factory tested units shall be fully assembled, tested and then split to accommodate shipment and job site rigging. | Comply | Units shall be shipped disassembled to the minimum module size in accordance with jobsite requirements for ease of rigging and installation.
| On units not shipped fully assembled, the manufacturer shall tag each section and include airflow direction to facilitate assembly at the job site. | Comply | All sections are marked. All details necessary for assembly of the sections are placed, adequately protected, inside one of the sections of the unit.
| Lifting lugs or shipping skids shall be provided for each section to allow for field rigging and final placement of unit. | Comply | Every module or mono-block unit has lifting holes
E. | The AHU manufacturer shall provide the necessary gasketing, caulking, and all screws, nuts, and bolts required for assembly. | Comply
F. | The manufacturer shall provide a local representative at the job site to supervise the assembly and to assure the units are assembled to meet manufacturer's recommendations and requirements noted on the drawings. | Assembly in Contractor's scope | DAIKIN engineer can be provided to supervise the installation (at extra cost)
| Provide documentation that this representative has provided this service on similar jobs to the Engineer. If a local representative cannot be provided, the manufacturer shall provide a factory representative. | Assembly in Contractor's scope | DAIKIN engineer can be provided to supervise the installation (at extra cost)
G. | Gaskets: All door and panel gaskets shall be high quality which seal airtight and retain their structural integrity and sealing capability after repeated assembly and disassembly of bolted panels and opening and closing of hinged components. | Comply | XLPE Reinforced foam tape TDS-will be provided on profile | Aerofoam XLPE chemically linked closed cell polyolefin foam composite, heat laminated to aluminum foil face & self adhesive. Thermal conductivity : 0.035 W/m.K at 24 C as per ASTM C518. Fire Rating : UL94, HF-1 Class 1 BS 476 Part 7 Class 0 BS 476 Part 6 ASTM E 84, Class A EN13501-1, B-s1, d0 comply Thermal conductivity & class HB according to UL 94.
| Bolted sections may use a more permanent gasketing method provided they are not disassembled. | Comply | XLPE Reinforced foam tape TDS-will be provided on profile
H. | Motor and Electrical Components: Refer to Section "Common Motor Requirements For HVAC Equipment." | Noted
I. | Air-handling units intended for outdoor installation shall be of the weather proof type. They shall have protective pitched roof and corrosion resistant paint finish. | Comply with Remarks | Flatroof / weatherproof canopy is provided as per scheduled data
J. | Air handling units with DX coils shall be completed with condensing units, specified separately in other sections. | Noted
8.4 | AIR HANDLING UNITS
A. | General: Provide factory-fabricated and factory-tested air handling units as indicated, sizes and capacities (cooling/heating) as shown on drawings. | Noted
| The precision unit shall be suitable for Data Computer rooms and Data Centers and to be installed indoors. | Not Applicable
| Units shall be tested, rated, and certified in accordance with AHRI 430 or EUROVENT. Unit shall bear AHRI or EUROVENT certification label and shall be listed in AHRI directory of Certified Applied Air Conditioning Products. | Comply | DAIKIN AHUs shall be with AHRI certified coils.
B. | For coastal areas environmental protection, Condenser coils shall be of copper fins and copper tubes. | Not Applicable
8.5 | GENERAL
A. | AHU casings shall be of double wall galvanized steel construction for indoor application and aluminium alloy construction for outdoor application. | Comply with Remarks | Unit casing shall be made of galvanized steel
B. | General Description: Factory assembled, consisting of fans, motor and drive, assembly, coils, damper, plenums, filters, drip pans, mixing box with dampers. | Noted | AHUs are selected as per scheduled data and datasheet including all relevant data is provided
C. | The Contractor and the AHU manufacturer shall be responsible for ensuring that the unit will not exceed the allocated space shown on the drawings, including required clearances for service and future overhaul or removal of unit components. | In Contractor's scope | AHU dimension shall be mentioned on datasheet
| All structural, piping, wiring, and ductwork alterations of units, which are dimensionally different than those specified, shall be the responsibility of the contractor at no additional cost to the Employer. | In Contractor's scope
D. | AHU sections shall be fully assembled by the manufacturer in the factory in accordance with the arrangement shown on the drawings. | Assembly in Contractor's scope | DAIKIN engineer can be provided to supervise the installation (at extra cost)
| The unit shall be assembled into the largest sections possible subject to shipping and rigging restrictions. | Comply | Units shall be shipped disassembled to the minimum module size in accordance with jobsite requirements for ease of rigging and installation.
| The correct fit of all components and casing sections shall be verified in the factory for all units prior to shipment. | Comply
| Factory tested units shall be fully assembled, tested and then split to accommodate shipment and job site rigging. | Comply | Units shall be shipped disassembled to the minimum module size in accordance with jobsite requirements for ease of rigging and installation.
| The units that are not shipped fully assembled, the manufacturer shall tag each section and include airflow direction to facilitate assembly at the job site. | Comply | All sections are marked. All details necessary for assembly of the sections are placed, adequately protected, inside one of the sections of the unit.
| Lifting lugs or shipping skids shall be provided for each section to allow for field rigging and final placement of unit. | Comply | Every module or mono-block unit has lifting holes
E. | The AHU manufacturer shall provide the necessary gasketing, caulking, and all screws, nuts, and bolts required for assembly. | Comply
F. | The manufacturer shall provide a local representative at the job site to supervise the assembly and to assure the units are assembled to meet manufacturer's recommendations and requirements noted on the drawings. | Assembly in Contractor's scope | DAIKIN engineer can be provided to supervise the installation (at extra cost)
| Provide documentation that this representative has provided this service on similar jobs to the Engineer. | Comply | IOM Manual is provided
| If a local representative cannot be provided, the manufacturer shall provide a factory representative. | Assembly in Contractor's scope | DAIKIN engineer can be provided to supervise the installation (at extra cost)
G. | Gaskets: All door and panel gaskets shall be high quality which seal airtight and retain their structural integrity and sealing capability after repeated assembly and disassembly of bolted panels and opening and closing of hinged components. | Comply | XLPE Reinforced foam tape TDS-will be provided on profile | Aerofoam XLPE chemically linked closed cell polyolefin foam composite, heat laminated to aluminum foil face & self adhesive. Thermal conductivity : 0.035 W/m.K at 24 C as per ASTM C518. Fire Rating : UL94, HF-1 Class 1 BS 476 Part 7 Class 0 BS 476 Part 6 ASTM E 84, Class A EN13501-1, B-s1, d0 comply Thermal conductivity & class HB according to UL 94.
| Bolted sections may use a more permanent gasketing method provided they are not disassembled. | Comply | XLPE Reinforced foam tape TDS-will be provided on profile
H. | Motor and Electrical Components: Refer to Section "Motors." | Noted
8.6 | REGULATORY REQUIREMENTS
A. | Comply with the requirements of Saudi Building Codes SBC, including and not limited to: | Noted
1. | SBC 201- Saudi Building Code- General; 2018. | Noted
2. | SBC 501- Saudi Mechanical Code; 2018. | Noted
3. | SBC 601- Saudi Energy Conservation Code Buildings except Low-Rise (Residential) | Noted
| Buildings; 2018. | Noted
4. | SBC 801- Saudi Fire Code; 2018. | Noted
5. | SBC 1001- Saudi Green Building Code; 2018. | Noted
B. | Comply with the Saudi Standards, Metrology, and Quality Organization SASO standards, and obtain the certificate of all products covered by this section (where applicable). | Noted
C. | Comply with the sustainability section 018113.13 Sustainable Design Requirements. | Noted
D. | Comply with NFPA 70. | Noted
E. | Products Requiring Electrical Connection: Listed and classified by UL (DIR) as suitable for the purpose specified and indicated. | Noted
F. | Certificate: AHU shall be AHRI or Eurovent certified. | Noted
G. | Comply with EXPRO Documents. | Noted
2.02 | GENERAL | Noted
A. | The chilled water coils shall be selected based on a working pressure of 1380 Kpa. | Noted
A. | The chilled water coils shall be selected based on a working pressure of 1380 Kpa. | Comply

## 9. Construction
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
9.1 | CONSTRUCTION
A. | Units shall be designed and constructed to minimise distortion, damage and drumming in operation and at the maximum pressures generated by the fan operating under closed head conditions. | Comply |  | The AHU casing is designed with double-skin panels with 62 mm thick CFC free PIR insulation (Polyisocyanurate insulation) sandwiched between outer and inner skin and adequate structural supports. Unit model box Casing Strength is rated as D1(M). The unit shall withstand fan shut-off (closed head) pressure without deformation, vibration, or drumming.
B. | The unit framework shall be rigid enough to prevent distortion during transportation and after final assembly on site. | Comply |  | The AHU casing is designed with double-skin panels and adequate structural supports. Unit model box Casing Strength is rated as D1(M). The unit shall withstand distortion during transportation and post assembly operations.
| Framework shall be fabricated from 3mm sheet steel unless otherwise stated. | Comply with Remarks |  | a) AHU Profile shall be made of extruded aluminum alloy
C. | Individual components and sections shall be assembled using proprietary and proven fastening techniques. Locking devices shall be used with all fastenings which are subject to vibration.
D. | Casings shall generally be of constant cross-sectional dimensions and designed to promote even air distribution across the face of all components.
E. | Casings shall be complete with internal flanged joints.
F. | Each section shall be identified by a clear stencil description on the external surface.
G. | Units shall be corrosion resistant and constructed free of condensation.
H. | Airtight seals shall be provided between the sections and completely around each access and unit panel. Jointing methods shall ensure the unit is not less airtight than the related ductwork system.
I. | Unit sections shall be fabricated from pressed multi-angled supports forming a pillar and post or box frame construction with purpose made corner joints. Rebates in the frame shall allow the access and infill panels to be flush with the frame and create a smooth surface inside and out.
J. | Panels shall be manufactured from heavy gauge galvanised mild steel sheets at least 1.2 mm thick. Panels shall be double skinned with high density acoustic and thermal insulation between the skins.
K. | The casing insulation properties:
1 | Compliant with BS 476-6:1989+A1:2009 and BS 476-7
2 | Adhesives and insulation materials shall have a composite fire and smoke hazard rating in compliance with NFPA 90A and UL 181 and labelled accordingly.
3 | CFC and HCFC free
4 | Inorganic, vermin proof and non-hygroscopic
5 | Unless otherwise indicated, minimum thickness shall be:
a. | 50 mm for units 1.0 m³/s or greater
b. | 25 mm for units less than 1.0 m³/s
c. | Thermal conductivity no greater than 0.03 W/mK
L. | Casing insulation shall be fixed securely to the panel and protected to prevent migration of fibre into the air flow.
M. | All insulation components shall be made from materials with zero ozone depletion potential (CFC and HCFC free). Submit to the CA, prior to ordering, written confirmation that the products to be installed are CFC, HFC and HCFC free.
N. | For all insulation infill material test evidence must be available and submitted to the CA showing that the fibres from which the products are made are not classified as a possible carcinogen as detailed by European Directive 97/69/EC. Fibres shall also comply with the requirements as stated elsewhere.
O. | Hollow section frame posts, where used, shall be insulated as for the casing.
P. | Thermal breaks shall be provided in the frame construction.
Q. | The design of the unit shall ensure that there is no cold bridging and no direct metallic contact between the inside and outside of the cabinets.
R. | External and internal casing finish and colour shall be as manufacturer’s standard unless stated otherwise elsewhere.
S. | Panels and frames shall be assembled with a closed cell self-adhesive neoprene foam gasket layer installed in between them to prevent air leakage, reduce vibration noise, minimized thermal losses.
T. | All panels shall be removable and sealed against the framework. The seal shall be mechanically fixed to the panel.
U. | Unless otherwise stated the minimum sound attenuation of the casing shall be:
Panel thickness
Hz 63 125 250 500 1K 2K 4K
50mm db 17 18 24 29 23 33 42
25mm db 22 26 26 37 38 39 47
V. | All section casings shall have the same cross-section and shall be identical in appearance
W. | Where units are large enough for man access the bottom/floor panels shall be suitably strengthened to facilitate entry for maintenance (support weight of two men, tools and equipment) without deformation and/or damage to internal finishes. The units shall have weatherproof bulkhead lighting and switches and non-slip floor surfaces. Lights shall be operable from inside and outside.
X. | Where flexible connections are mounted within the air handling unit they shall be to the same specification as described elsewhere.
Y. | Visual inspection port holes shall be provided of at least 200 mm diameter and one per 900mm height of section in each of the following sections unless otherwise stated:
1 | Fan section
2 | Humidifier section
3 | Access sections
4 | Cooling coil section
Z. | Bulkhead lighting shall be provided and each bulkhead light shall be wired to its own internal and external on/off switch in each of the following sections:
1 | Fan section
2 | Humidifier section
3 | Access sections
4 | Cooling coil section
AA. | The unit shall be delivered on a base frame constructed from galvanised steel. The base frame shall be pre-drilled for fixing holding down bolts and shall have removable lifting lugs.
BB. | Air intake louvres shall prevent the ingress of rain and sand and shall incorporate an insect screen. The colour and finish shall be approved by the CA prior to manufacture.
9.1.1 | EXTERNAL UNITS
A. | Where units are located externally they shall be weatherproofed including associated control panels.
B. | Units shall have a weatherproof outer casing with a pitched roof constructed of watertight metal decking with water seals in all joints having suitable eaves overhang and complete with gutters and drains.
C. | The casings of all external units exposed to a saline environment (within 20km of the sea, unless stated otherwise) shall be designed and tested to withstand 500 hours salt spray exposure in accordance with ASTM B117.
D. | Access doors shall be lockable.
E. | Bulkhead light fittings shall be provided in each section with a weatherproof external switch with all wiring contained in galvanised mild steel conduit.
9.2 | CONSTRUCTION
1 | AHUs shall be entirely of double wall galvanized steel construction. Galvanizing shall be hot dipped conforming to A653/A653M and shall provide a minimum of 0.275 kg of zinc per square meter (0.90 oz. of zinc per square foot) (G90). Aluminum constructed units may be provided subject to the Engineer’s approval and documentation that structural rigidity is equal or greater than the galvanized steel specified.
2 | Air handling unit shall be with removable panels for accessibility to all internal parts.
3 | The unit panels skin thickness should be not less than 0.7 mm for outer and inner skin. The panels shall be fabricated of galvanized sheet. (or aluminum if structural rigidity is equal or greater than the steel).
4 | All access doors shall be insulated to the same standard as the unit casing open towards the high pressure side.
5 | Full size hinged access doors with cam-locks and fixed handles should be provided for inspection section, filters section, electric heaters section & fans section.
6 | Walk in units should have internal door handles and reinforced floors.
7 | Air handling unit intake and discharge openings should be fitted with a flanged duct connection frame.
8 | All panels should be removable from outside the casing with quick release fasteners and sturdy handles. the inspection doors should be hung on adjustable hinges and equipped with mechanical secured sealing strips against the framework and view window. The sealing strips should be of cellular rubber with closed pores. The panel shall be mounted flush with the frame members to create a smooth surface inside and outside.
9 | Unit(s) installed indoor shall be factory insulated internally with polyurethane foam 40mm. thick or approved equivalent and finished with oven dried gray finishing coat.
10 | Outdoor exposed units shall be of the double skin type factory insulated with 60mm polyurethane foam. thick or approved equivalent and finished with oven dried marine gray finishing coat suitable for outdoor application with anti corrosion coating.
11 | Outdoor exposed unit shall have additional sheet roof steel with epoxy coated finish with a minimum of 150mm air space above the top panel and angled at a minimum slope of 1:50. The roof shall overhang all sides by a minimum of 150mm.
12 | Outdoor exposed unit shall have the inner and outer panel skin should be coated with minimum of 7 micro primer + 20 micro polyester + 10 micro epoxy paint or reverse side. The walls from inside and outside should be completely smooth.
13 | The installer shall provide the flexible duct connection and ensure that the duct is suitably supported to ensure no deformation.
14 | The deflection of the panel must not exceed 4 mm per metre under maximum fan operating pressure (Eurovent EN1886 D1 class or AHRI 1350 CD1 class).
15 | Thermal Conductance (C): Maximum overall thermal conductance of casing (panel and structure) shall be T2 Class as per EN1886 or AHRI CT2 class.
16 | Casing air leakage shall be L1(M) class as per EN1886 or AHRI CL1 class.
17 | Condensation Requirements: Provide cold bridge free construction to protect the unit against condensation. The casing must meet the requirements of Eurovent EN1886 TB1.
18 | Filter Housing: Provide front loading type filter holding frames with clips to minimize filter bypass leakage on filter holding frame to F9 class as per EN1886.
19 | The coil shall be accessible for service and shall be removable without dismantling the entire unit. The face velocity shall not exceed 500 FPM. (2.55 m/s).
9.3 | CONSTRUCTION
A. | Units shall be designed and constructed to minimise distortion, damage and drumming in operation and at the maximum pressures generated by the fan operating under closed head conditions.
B. | Each air handling unit section shall have a heavy duty, fully welded, chassis frame fabricated from rectangular hollow section aluminium steel tube, reinforced and stiffened where necessary to provide a rigid frame work.
C. | Panels shall be manufactured from heavy gauge galvanised mild steel sheets at least 1.2 mm thick.
Panels shall be double skinned with heavy density acoustic and thermal insulation between the skins.
D. | The casing insulation properties:
1 | . Compliant with BS 476 -6 and BS 476-7
2 | CFC and HCFC free
3 | Inorganic, vermin proof and non-hygroscopic
4 | Unless otherwise indicated, minimum thickness shall be:
5 | 50 mm for units 1.0 m3/s or greater and all external located units
6 | 25 mm for units less than 1.0 m 3/s where installed in air conditioned plantrooms
7 | Thermal conductivity no greater than 0.03 W/mK
E. | Casing insulation shall be fixed securely to the panel and protected to prevent migration of fibre into the air flow.
F. | All insulation components shall be made from materials with zero ozone depletion potential (CFC and HCFC free). Submit to the Engineer, prior to ordering, written confirmation that the products to be installed are CFC and HCFC free.
G. | For all insulation infill material test evidence must be available and submitted to the Engineer showing that the fibres from which the products are made are not classified as a possible carcinogen as detailed by European Directive 97/69/EC. Fibres shall also comply with the requirements as stated elsewhere and with HSE guidelines. The Insulation shall comply with Ml fire class according to the technical laboratory CSTB
H. | Each section shall be identified by a clear descriptive label on the external surface.
Air handling unit sections shall be mounted on a common rolled steel channel base frame construction, completely welded to provide a rigid construction. The clearance between the underside of the AHU and finished grade level shall not less than 300mm.
J. | Insulation shall be factory applied and contained within an impervious membrane designed to last the life of the AHU.
K. | Any surface liable to condensation formation shall be insulated and provided with a vapour barrier. Where free moisture may be present, a waterproof membrane shall be provided.
L. | Readily removable access panels or hinged doors complying with DWI 144, incorporating air seals shall be provided to facilitate access to upstream and downstream faces and internal parts of all sections in the AHU.
M. | Access panels shall be provided wherever indicated on the design drawings and in addition shall be provided to allow all large items of plant such as coils, fans, motors and the like to be easily removed. Access doors shall be of sufficient size to allow reasonable man access and the passage of tools and equipment required for the replacement of these items.
N. | The overall appearance of the unit, including such access panels, shall be of a flush finish on the top and the sides and varying heights and widths of components will not be allowed.
O. | Access panels shall be secured with a minimum number of proprietary quick-release captive fastenings consistent with effective air sealing. Hinged doors shall be retained with clamping type latches. Access panels and hinged doors shall be 500mm wide minimum and sized for the full height of the AHU or be 1.35m maximum. Self-tapping screws and set screws are not acceptable as panel fastening. Access doors to components or access chambers shall be fixed with floating hinges as detailed elsewhere and shall be arranged to allow the access door to move away from the unit before the door swings open to prevent damage to the gasket sealing system. The doors shall clamp without imposing a strain on these hinges. All sealants and gaskets shall comply with water research association requirements for the non-support of bacterial growth.
P. | Protection shall be provided to avoid damage to insulation in sections having walk-in access. Floor decking, suitable for 1.5kN/m2 loading, shall be provided to all accessible sections.
Q. | Sections of AHU's shall be arranged with adequate separation to avoid evaporation of condensate from the cooling coil by the heating coil and generally to promote even air distribution across the face of all components.
R. | Units shall have corrosion-resistant drain trays of adequate size to collect waste water. These shall be extended as necessary, or other means of collection provided, to drain away any water deposited or condensed in adjacent sections. Drain trays shall be provided with drain connections and traps. Where the drain tray forms the outer surface of the AHIJ, the outer surface shall be insulated and vapour sealed.
S. | Airtight sleeves shall be provided for control sensors, instruments and test holes.
T. | Sections of each air handling unit likely to contain components producing moisture i.e. cooling coils shall have double skinned insulated bottom panels which slope to a plugged drain socket built into the side of the bottom member such that moisture will drain off in the event of an overflow emergency from the normal drip trays. The inner surface of such panels shall be finished with a high build bitumastic sprayed paint.
U. | Each air handling unit shall be delivered to site and be pre-wired for internally mounted controls and bulkhead lights. Lights shall be installed in the unit within all main sections and shall be of a fully waterproof bulkhead type fully suitable for their application. The lights shall be suitable for a 24 volt AC supply and shall be fully pre-wired to a terminal box and transformer on the outside of the units for connections on site by the Controls Specialist to the relevant motor control centre power ring circuit.
V. | All such conduits required shall be in galvanised steel. One such junction box will be required per air handler. The air handler manufacturers shall include all necessary pre-wiring and site conduit installations, and the sizing and installation of suitable transformer to accept 220 volt incoming supply.
W. | Inspection ports shall be no less than 200mm diameter and shall be of the double-skinned type and shall be provided on all main sections of the AHU.
X. | In addition the air handling unit manufacturers shall liaise with the Contractor to make themselves fully aware of any control items such as temperature detectors, filter pressure switches, air flow switches and the like as required.
Y. | The air handling unit manufacturers shall allow for all necessary pockets or internal pneumatic tubing and shall allow for factory fitting and air testing of the same.
Z. | Finally 50mm screwed fumigation points shall be provided at 2 No. locations (either side of each cooling coil) and these shall be complete with a sealing gasket and blanking cap and be of brass manufacture.
9.3.2 | OUTDOOR UNITS
A. | AHU's for outdoor installation shall have a weatherproof outer casing, a pitched roof constructed of watertight metal decking with water seals in all joints and lockable access doors.
B. | Bulkhead light fittings shall be provided in each section with a weatherproof external switch and all wiring in galvanised mild steel conduit. Penetrations through the casing made for cabling, controls and other ancillary equipment shall be airtight and weather tight and purpose made during manufacture.
9.4 | BASE
A. | Provide a heavy-duty steel base for supporting all AHU major components. Bases shall be constructed of wide-flange steel I-beams, channels, or minimum 152 mm (6 inch) high 3.5 mm (10 gauge) steel base rails. Welded or bolted cross members shall be provided as required for lateral stability. The Contractor shall provide supplemental steel supports as required to obtain proper operation heights for cooling coil condense drain trap as shown on drawings.
B. | AHUs shall be completely self-supporting for installation on concrete housekeeping pad, steel support pedestals, or suspended as shown on drawings.
C. | The AHU bases not constructed of galvanized material shall be cleaned, primed with a rust inhibiting primer, and finished with a rust inhibiting exterior enamel.
D. | Seismic Fabrication Requirements: Fabricate mounting base and attachment to air-handling unit sections, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC" when air-handling unit frame is anchored to building structure.
9.4.2 | CABINET
A. | General: AHU shall be designed and constructed such that removal of any panel shall not affect the structural integrity of the unit. Plug panels may be used to enhance structural stability provided access space is not reduced.
B. | Materials: Formed and reinforced, double wall construction, galvanized steel panels, fabricated to allow removal for access to internal parts and components, with joints between sections sealed. The outer walls of the double skin panel shall be precoated with oven backed polyester paint finish. Units for outdoor installation shall have protective pitched roof and corrosion resistant paint finish.
Units with 100% outdoor air shall have internal sides protected with corrosion resistant paint finish.
1 | Outside Casing: Galvanized steel, 1.3 mm.
2 | Inside Casing: Galvanized steel, 1 mm.
3 | Floor Plate: Galvanized steel, 3.5 mm.
C. | Thermal Conductance (C): Maximum overall thermal conductance of casing panels shall not exceed 0.68 W/square meter. K (0.12 Btu/ (h. square feet. degree F)).
D. | Condensation Requirements: AHUs shall be designed to ensure that there is no condensation on the exterior of the unit based on outside design conditions. Through metal connections between inner and outer panels shall be kept to an absolute minimum. If tubular structural members are used inside of tube shall be insulated equal to casing.
E. | Unit sections shall be tightly joined in the field through the use of all-thread rod or casing brackets and shall be gasketed to make airtight.
F. | Exterior and interior panels shall be secured to the support channels with stainless steel screws and gaskets installed around the panel perimeter. Screw spacing shall not be greater than 229 mm (nine inches). Panels shall be completely removable to allow removal of fan, coils, and other internal components for future maintenance, repair, or modifications. Welded exterior panels are not acceptable.
G. | Provide sealed sleeves, metal or plastic escutcheons or grommets for penetrations through casing for power and temperature control wiring and pneumatic tubing. Coordinate number and location with electrical and temperature control subcontractors. Coordinate lights, switches, and duplex outlets and disconnect switch location and mounting. All penetrations and equipment mounting shall be provided in the factory. All field penetrations shall be performed neatly by drilling or saw cutting. No cutting by torches will be allowed. Neatly seal all openings airtight.
H. | Insulation: CFC free polyurethane insulation, complying with NFPA 90A flame spread and smoke generation requirements, "Installation of Air Conditioning and Ventilating Systems," for insulation.
1 | The walls, roof and floor of the AHU shall be insulated. Insulation shall be held securely in position between the inner and outer skin of casing.
2 | Thickness: 50 mm.
3 | Insulation shall have 44 kg/cubic meter minimum density rigid glass fiber. Insulation shall meet ASTM C1071 requirements.
4 | Location and Application: Factory applied with adhesive and mechanical fasteners to the internal surface of section panels downstream from and including the cooling coil section.
I. | Access Panels and Doors: Same materials and finishes as cabinet and complete with hinges, latches, handles, and gaskets. Provide in each access section. Doors shall be a minimum of 600 mm (24 inches) wide and shall be the full casing height up to a maximum of 1850 mm (6 feet). Doors shall be gasketed, hinged, and latched to provide an airtight seal. Each door shall include a minimum 150 mm x 150 mm (6 inch x 6 inch) double thickness reinforced glass or Plexiglas window in a gasketed frame.
1 | Hinges: Manufacturers standard, designed for door size, weight and pressure classifications. Hinges shall hold door completely rigid with minimum 45 kg (100 pound) weight hung on latch side of door.
2 | Latches: Non-corrosive alloy construction, with operating levers for positive cam action, operable from either inside or outside. Doors that do not open against unit operating pressure shall be provided with safety "Vent lock"style latches which allow the door to open approximately 75 mm (3 inches) and then require approximately 0.785 radian (45 degrees) further movement of the handle for complete opening. Latch shall be capable of restraining explosive opening of door with a force equal to a minimum of 2986 Pa (12 inches water) of differential static pressure or 1-1/2 times operating differential pressure whichever is greater.
3 | Gaskets: Neoprene, continuous around door, positioned for direct compression with no sliding action between the door and gasket. Secure with high quality mastic to eliminate possibility of gasket slipping or coming loose.
4 | Fan section shall have inspection and access panels and doors sized and located to allow periodic maintenance and inspections.
J. | Floor:
1 | Unit floor shall be level without offset space or gap and designed to support a minimum of 488 kg/square meter (100 pounds per square foot) distributed load without permanent deformation or crushing of internal insulation.
2 | Provide adequate structural base members beneath floor in service access sections to support typical service foot traffic and to prevent damage to unit floor or internal insulation.
3 | Unit floors in casing sections, which may contain water or condensate, shall be watertight with drain pan.
4 | Thermal Conductance (C): Maximum overall thermal conductance of casing floors shall not exceed 0.68 W/square meter. K (0.12 Btu/ (h. square feet.
degree F)).
K. | Drain Pans: Formed sections of insulated stainless steel (316), sheet based. Fabricate pans in sizes and shapes to collect condensate from cooling coils (including coil piping connections and return bends) when units are operating at maximum cataloged face velocity across cooling coil. Depth of drain pan shall be at least 43 mm (1.7 inches) and shall handle all condensate without overflowing. Drain pan shall be sloped to drain. Drain pan shall be continuous metal or welded watertight. No mastic sealing of joints exposed to water will be permitted. Drain pan shall be placed on top of casing floor or integrated into casing floor assembly.
Maximum overall thermal conductance of floor/drain pan assembly shall not exceed 0.68 W/square meter K (0.12 Btu/ (h. sq. ft. degree F)).
1 | Double-Wall Construction: Fill space between walls with foam insulation and seal moisture tight.
2 | Drain Connections: Both ends of pan.
3 | Pan-Top Surface Coating: Elastomeric compound.
4 | Units with stacked coils shall have an intermediate drain pan or drain trough to collect condensate from top coil.
5 | Cooling coil ends shall be enclosed by cabinet and shall be factory insulated against sweating or shall drain to a drain pan.
6 | All pans shall have a double slope to the drain point.
L. | Electrical and Lighting: Wiring and equipment specifications shall conform to Division 26 Sections.
1 | Provide factory installed vapor-proof lights using cast aluminum base style with glass globe and cast aluminum guard shall be installed in each access section, fan, coil, filter and mixing box sections.
2 | A switch shall control the lights in each compartment with pilot light mounted outside the respective compartment access door. Wiring between switches and lights shall be factory installed. All wiring shall run in neatly installed electrical conduits and terminate in a junction box for field connection to the building system. Provide single point 230 volt - one phase connection at junction box.
3 | Install compatible 100 watt bulb in each light fixture.
4 | Provide a convenience duplex outlet next to the light switch.
5 | Disconnect switch and power wiring: Provide factory or field mounted disconnect switch. Coordinate with Electrical Specifications.
M. | Inspection Windows: Provide factory installed 150mm glass inspection windows on fan and filter plenum section access panels of air-handling units.
9.5 | Casings
C. | Casings: Component modules shall be 50 mm thick constructed of sectionalized, mill galvanized steel formed double skin insulated panels, rigidly reinforced with external structural steel frame. Provide hinged access doors with neoprene type door gasket for access to sections and components requiring servicing. All units installed externally shall have close cell self-adhesive neoprene foamed gasket joints k value of 0.4 W/mo K between panels. Externally mounted units shall have a pitched roof with extra anticorrosive paint and self-adhesive protection foil.
D. | Insulation: Coil, fan and accessory section panels shall be secured to casing with permanent fasteners and shall meet NFPA 90A flame spread and smoke generation requirements. All units shall be double skinned construction with 50 mm thick thermal and acoustic insulation injected polyurethane having thermal coefficient of 0.5 W/mo K.
9.6 | CASING CONSTRUCTION
A. | Full Perimeter Base Rail:
1. | Construct of galvanized steel.
2. | Provide base rail of sufficient height to raise unit for external trapping of condensate drain pans.
B. | Casing:
1. | Construct of one piece, insulated, double wall panels.
2. | Provide mid-span, no through metal, internal thermal break.
3. | Construct outer panels of galvanized steel and inner panels of galvanized steel.
4. | Casing Air Pressure Performance Requirements:
a. | Able to withstand up to 2 kPa positive or negative static pressure.
b. | Not to exceed 0.000165 mm per mm deflection at 1.5 times design static pressure up to a maximum of plus 2 kPa in positive pressure sections and minus 2kPa in negative pressure sections.
C. | Access Doors:
1. | Construction, thermal and air pressure performance same as casing.
2. | Provide surface mounted handles on hinged, swing doors.
3. | Provide shatterproof viewing window designed to withstand operating pressures.
D. | Outdoor Unit Roof:
1. | Factory install single layer outer roof above inner roof.
2. | Slope at a minimum of 10.41 mm per m from one side of unit to the other side, or from center to sides of unit.
3. | Roof assembly to overhang each unit wall or base rail to overhang curb to facilitate water runoff and prevent water intrusion into roof curb to base connection.
E. | Outside Air and Exhaust Air Weather Hood:
1. | Fabricate from same material as casing outer panel.
2. | Extend hood past perimeter of unit casing opening so as not to instruct airflow path.
3. | Paint hoods with same finish as external surface of outdoor units.
4. | Provide inlet hood for each fresh air damper with a sine wave moisture eliminator to prevent entrainment of water into the unit from outside air.
5. | Provide exhaust hoods for each exhaust air opening.
6. | Size each hood for 100 percent of nominal fresh air damper capacities.
7. | Protect each hood with bird screen to prevent nesting at intake or exhaust airflow paths.
F. | Unit Flooring: Construct with sufficient strength to support expected people and equipment loads associated with maintenance activities.
G. | Casing Leakage: Seal joints and provide airtight access doors so that air leakage does not exceed one percent of design flow at the specified casing pressure.
H. | Insulation:
1. | Provide minimum thermal thickness of 2.29 RSI throughout.
2. | Completely fill panel cavities in each direction to prevent voids and settling.
3. | Comply with NFPA 90A.
I. | Louvers: Stationary, of galvanized steel, 100 mm deep with plenum, nylon bearings, 13 mm mesh, 1.0 mm galvanized wire bird screen in aluminum frame, and bearing AMCA
Certified Ratings Seal in accordance with AMCA 500-L. Furnish adjustable louvers with hollow vinyl bulb edging on blades and foam side stops to limit leakage to maximum 2 percent at 1 kPa differential pressure when sized for 10 m/s face velocity.
J. | Marine Lights:
1. | Provide factory-mounted, water- and dust-resistant LED fixture(s), with the following characteristics:
a. | Non-ferrous metal housing.
b. | Glass or polycarbonate lens.
c. | Factory wired to a single switch within factory provided service module.
d. | Instant on white light with minimum 8,000 hour service life.
2. | Provide factory installed service module including GFCI receptacle independent from load side; designed to receive power from single-point power source.
K. | Finish:
1. | Outdoor Units:
a. | Coat external surface of unit casing with primer and minimum 1.5 mil, enamel paint finish.
b. | Comply with salt spray test in accordance with ASTM B177/B177M.
c. | Color: Manufacturer's standard color.
2. | Indoor Units:
a. | Provide exterior, galvanized steel panels with painted surface complying with ASTM B177/B177M.
b. | Color: Manufacturer's standard color.

## 10. Dampers & Mixing Box
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
10.1 | DAMPERS
A. | Unless otherwise stated dampers shall be double skin aerofoil multi-leaf opposed blade, fabricated from stainless steel with maintenance free nylon bearings and complete with suitable linkages. Unless otherwise indicated, air leakage through dampers when in the closed position shall not exceed 5% of the maximum design air volume flow rate at the maximum design air total pressure.
B. | Each damper section shall be provided with a duct connection flange.
C. | Mounting brackets and actuators shall be supplied by the controls specialist
10.1.1 | MIXING BOXES/DAMPER SECTION
A. | Mixing box sections shall be supplied having double skin aerofoil parallel blade dampers positioned across each air opening fabricated from stainless steel with maintenance free nylon bearings and complete with suitable linkages.
B. | On fixed quantities of mixed air, dampers shall be sized to give equal velocities through each damper.
C. | Hinged access doors shall be provided into the damper mixing box section.
D. | Each damper section shall be provided with a duct connection flange.
E. | Mounting brackets and actuators shall be supplied by the controls specialist
10.2 | ACCESS SECTION
A. | Access sections shall be provided with hinged doors to allow entry for internal inspection purposes.
B. | Access sections shall be provided to facilitate access to upstream and downstream faces and internal parts of all sections in the unit including thermostat, detector, air-flow switch and other control/monitoring positions within the unit.
C. | Access panels and hinged doors shall be 600mm wide minimum and sized for the full height of the AHU.
D. | Access panels shall be secured with proprietary quick-release captive fastenings consistent with effective air sealing. Hinged doors shall be retained with clamping type latches.
E. | Self-tapping screws and set screws shall not be acceptable as panel fastening
F. | Quick release and totally removable access door shall be provided at filter sections with side rail mounting.
G. | All seals shall be designed for normal maintenance operations for a minimum of 10 years
10.3 | DAMPERS
A. | Outdoor-Air Damper: Linked damper blades, for 0 to 25 percent outdoor air, with motorized damper filter. Motorised dampers shall be of the multi-leaf type. Blades shall be limited in length to prevent twisting, vibration or binding during operation. Each set of blades shall interlock when closed. Blade attachment to spindles shall be by a positive mechanical connection. Spindles shall be mounted in bearings.
B. | Dampers to be mechanically fastened to cadmium plated for galvanized-steel operating rod in reinforced cabinet. Connect operating rods with common linkage and interconnect linkages so dampers operate simultaneously.
1 | Damper Motor: Modulating with adjustable minimum position.
2 | Relief-Air Damper: Gravity actuated or motorized, as required by ASHRAE/IESNA 90.1-2004, with bird screen and hood.
C. | Damper assemblies shall be of corrosion resistant materials to suit the application and shall be electrolytically compatible.
D. | Motorised dampers shall be constructed to withstand the differential pressures without permanent distortion and when the dampers are closed.
E. | Damper leakage shall not exceed 20 l/s.m2 at 500 Pa.
F. | Linkage systems shall transmit torque to blades so that they move equally. Linkage system shall be arranged to eliminate any 'slack' movement. Linkage systems type shall be geared.
G. | Damper actuators shall be of the direct-coupled direct-transmission type, clamped to the blade spindle and secured to prevent motor rotation. A rigid mounting bracket shall be provided for each damper actuator. Each damper module shall have at least one actuator and where more than one actuator is provided their operation shall be synchronised.
H. | Dampers shall be sized to provide a linear characteristic over the full operating movement of the damper, unless otherwise indicated.
The fresh air intake exhaust air, isolation damper blades, mechanisms and frames shall be made from stainless steel (316L) and shall be parallel double skin aerofoil blade (maximum closed leakage at system pressure of two percent). Parallel blade dampers are required for linear control characteristics.
J. | All dampers shall be air tight shut off, to assist with building air leakage testing.
K. | All motor drives for dampers shall be mounted external to the air handling units.
L. | The Contractor should note that the dampers may require multiple actuators, and they shall be costed for after consultation with the AHU supplier. Where multiple actuators are required it may also be necessary to sequence the operation of the damper. The Contractor shall liaise with the Controls Specialist to ensure that this is included, where required.
M. | All mixing damper arrangements shall be as detailed above, using opposed double skin aerofoil blades.
10.4 | DAMPERS
A. | General: Leakage rate, according to AMCA 500-D, "Laboratory Methods of
Testing Dampers for Rating," shall not exceed 2 percent of air quantity at 10-m/s (2000-fpm) face velocity through damper and 1000-Pa (4-inch wg) pressure differential.
1 | Damper operators shall be electrically operated.
2 | Damper operators are specified in Section "Building Management System."
B. | Face and Bypass Dampers: Opposed-blade galvanized steel dampers, with steel operating rods rotating in sintered bronze or nylon bearings mounted in a single galvanized steel frame, and with operating rods connected together with a common linkage. Break-form damper blades, provide gaskets and edge seals, and mechanically fasten to operating rod.
C. | Mixing Boxes: Parallel-blade galvanized steel damper blades mechanically fastened to steel operating rod in reinforced, galvanized steel cabinet. Connect operating rods with common linkage and interconnect linkages so dampers operate simultaneously.
D. | Combination Filter/Mixing Box: Parallel-blade galvanized steel damper blades mechanically fastened to steel operating rod in reinforced, galvanized steel cabinet. Connect operating rods with common linkage and interconnect linkages so dampers operate simultaneously. Cabinet support members shall hold 50-mm thick, pleated, flat permanent or throwaway filters. Provide hinged access panels or doors to allow removal of filters from both sides of unit.
10.5 | DAMPER SECTION
A. | Mixing Section: Provide a functional section to support the damper assembly for modulating the volume of outdoor, return, and exhaust air.
B. | Damper Blades:
1. | Double-skin airfoil design with metal, compressible jamb seals and extruded-vinyl blade-edge seals on each blade.
2. | Self-lubricating stainless steel or synthetic sleeve bearings.
3. | Comply with ASHRAE Std 90.1 I-P for rated maximum leakage rate.
4. | Provide leakage testing and pressure ratings in compliance with AMCA 500-D test methods.
5. | Arrange in parallel or opposed-blade configuration.

## 11. Filters
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
11.1 | FILTERS
A. | Filters within air handling units shall be as detailed elsewhere and shall operate with not less than the efficiencies specified.
B. | Filter performance shall be measured in accordance with Eurovent standard 4/5 and BS EN 779.
C. | Face velocities across filters shall be limited to a maximum of 2 m/s.
D. | Filter unit or panels shall be selected to be of uniform size and pressure drop
E. | Filter media shall not be subject to erosion, deterioration or to the effects of temperature and shall be manufactured from non-deleterious materials.
F. | Filter material shall be non-hygroscopic, shall not support vermin and shall be proof against fungal and bacterial growth and attack.
G. | Filters shall be non-flammable and comply with BS 476.
H. | Frames, casings and filter cell holding frames shall be classified non-combustible when tested in accordance with BS 476.
I. | When exposed to heat or flame, the filter shall not generate significant quantities of smoke or toxic fumes into the air-stream.
J. | Filter material or wetting agents shall not be carried over in the air-stream.
K. | Adequate access shall be provided for cleaning, removal and refitting of all filter cells and replacement of gaskets in filter holding frames.
L. | Combined pre-filters and main filters shall each be capable of being changed without disturbing the other filter
M. | Filters shall be complete with robust purpose made holding frames which shall not distort in operation and with seals to prevent air leakage or bypass.
N. | Purpose made seals shall be provided to minimise air leakage around filters and the effectiveness of the seals shall not be impaired by periodic removal and refitting of the filter cells.
O. | The entire framework shall be securely fixed in position with all edges and joints effectively sealed to prevent air leakage.
P. | Subsequent to commissioning and immediately prior to practical completion all disposable filters shall be replaced. In addition one complete set of replacement media shall be provided for each disposable filter. For cleanable units, sufficient replacements of each size and type to allow individual units to be changed shall be provided. Where disposable filters are attached to mounting grids or frames, other than by quick release fastenings, sufficient frames shall be provided to meet the above requirements.
Q. | A copy of the type test certificate, issued by a NAMAS accredited air filter testing laboratory, shall be submitted to the CA for each type of filter.
R. | Filter Mounting Frame:
1 | Mounting frames shall be manufactured from galvanized steel and designed to ensure that the filter can be accessed.
2 | Frame mounting frame or rails shall be sealed for a minimal air leak Class F5-7 according to EUROVENT Standard EN 779.
S. | Primary/Pre Filter:
1 | Pre-filters shall be arranged in flat or angle bank configuration, applicable to the required duty and each cell shall consist of a pleated synthetic fibre element bonded to prevent fibre migration and impregnated with special adhesive. The element shall be supported by a galvanised wire mesh backing and enclosed within a stout fibre board frame with integral grid for added reinforcement.
2 | The average arrestance shall be 87% when tested in accordance with BS EN 779 class G3 or G4 as stated elsewhere.
3 | Filters shall be contained in a standard air handling section and arranged for front or side withdrawal depending upon space limitations.
4 | Panels shall be of the disposable type unless otherwise indicated.
T. | Secondary filters
1 | High capacity bag filters shall be arranged in a flat bank and shall comprise a permanent corrosionresistant holding frame housing a synthetic fire retardant media.
2 | The media cartridge shall be pre-formed and shall be in accordance with BS EN 779 class F7 with an average efficiency of 80-90% or class F9 with an average efficiency of 95% as indicated elsewhere.
3 | Filters shall be capable of remaining fully inflated within the airstream.
4 | Filters shall be contained in a standard air handling section and withdrawal/access shall be as indicated
U. | Activated carbon filters
1 | Activated carbon filters shall comprise cells containing activated carbon granules selected to suit the contaminants as indicated elsewhere.
2 | Evidence as to both efficiency and adsorption capacity of the adsorbent at the indicated levels shall be submitted to the CA for acceptance.
3 | Air filters shall comprise of absorbent bed filled with uniform thickness of activated carbon granules, constructed to prevent settlement and voids do not occur.
4 | The media shall be of a disposable or reactivated type as indicated and housed in a permanent corrosion resistant holding frame. Cell construction shall include provision to prevent migration of the filter media.
5 | Each filter assembly shall include two detachable test sections for use in predicting the service life of the filter assembly. The test sections shall be exposed to full air flow and be removed and replaced by a spare after 6 and 12 months operation and returned to the manufacturer for analysis of saturation and report on service life remaining. The Contractor shall be responsible for this removal and replacement during the defects liability period and shall include for the spares, the manufacturer's costs for the analysis/report shall be included in the contract cost. Allowance shall be made for housing the test sections as part of the filter assembly.
6 | All metallic parts shall be adequately protected against corrosion.
7 | Filters shall be contained in a standard air handling section and shall have withdrawal facilities as indicated.
V. | Filter Manometers
1 | All filters shall be provided with an inclined manometer or differential pressure gauge which shall indicate the actual pressure drop across the filter.
2 | The filter clean and dirty pressures shall be indicated.
3 | Where dirty filter monitoring is provided, each filter shall have a pressure sensor to indicate to the control panel or BMS, as appropriate, filter dirty conditions.
11.2 | AIR FILTRATION
A. | Filters within air handling units shall be as detailed elsewhere and shall operate with not less than the efficiencies specified.
B. | Filter performance shall be measured in accordance with Eurovent standard 4/5 and BS EN 779. Air velocity at the filter face shall not exceed 2.5m/s and panel and bag filter shall be provided within each
C. | Filters classes shall be selected to suit the application. Where panel and bag filters are fitted in series the minimum class provided shall be:
D. | Panel Filters
1 | The average arrestance shall be 87% when tested in accordance with BS EN 779 clause G3 or G4 as stated elsewhere.
2 | Final pressure drop shall not exceed: 170Pa clean and 250Pa dirty.
E. | Bag or Extended Surface Type Filters
1 | . The media cartridge shall be pre-formed and shall be in accordance with BS EN 779 class F7 with an average efficiency of 80-90% or class F9 with an average efficiency of 95% as indicated e I sevvhere.
2 | Final pressure drop shall not exceed: 250 Pa clean and 350 Pa dirty.
3 | Filters shall be fully self-supporting without external ties or stiffening frames. Filters shall inflate fully, shall not sag or flutter, nor have effective medium area reduced by obstruction due to contact with other filter faces or housing surfaces when operating between 60% and 1 10% of design air volume flow rate for fixed volume systems.
4 | Filter length shall not exceed 760mm.
F. | General
1 | Filter material or wetting agents shall not be carried over in the air stream.
2 | Adequate access shall be provided for removal and refitting of filter cells or replacement of gaskets in filter holding frames.
3 | Filter differential pressure indication shall be provided for each filter assembly.
4 | Filter assemblies including casings, filter media, protective cappings and sealing gaskets shall be of materials compatible with the system operating environment. Casings shall not warp, splinter or corrode.
5 | Filter cell holding frames shall be purpose-made from non-ferrous metal, plastic, or steel protected against corrosion, of adequate strength and stiffened to prevent distortion in use.
6 | Holding-down frames shall be capable of retaining air filters in a rigid manner and shall be securely fixed in position with all edges and joints effectively sealed to prevent air leakage.
7 | Purpose-made gaskets shall be provided to minimise air leakage around the filters. The effectiveness of the seal shall not be impaired by removal and refitting of filter cells. Gasket material shall be fitted in the holding frames.
8 | Retaining clips, or other securing devices, shall be capable of pulling the filter on to its seating and shall exert equal pressure on all faces.
9 | The air handling unit manufacturer should specifically note the requirements for access for filter removal and he shall allow for providing suitably calibrated pressure differential gauges to the filter sections which shall be fully pre-piped and fitted to the air handling unit frames in addition to the electronic sensors mentioned earlier. These gauges shall be complete with engraved marker plates positioned alongside to detail filter normal and dirty pressure drops and shall also be engraved on the gauge themselves with the dirty pressure drop.
10 | The air handling manufacturer shall include for a complete set of filters for installation following commissioning and a complete set of spare filters which shall be handed over to the Client at project handover for installation into the air handling units.
11 | The Mechanical Sub-Contractor shall include for the removal and disposal of the dirty filter media and for the installation of the clean filter media when the Project is handed over.
G. | Fire Properties
1 | Filter media (other than for adsorption filters), all materials of construction, adhesives, coatings and wetting agents shall permanently retain self-extinguishing properties. Surfaces of filters shall be non flammable.
2 | When exposed to heat or flame, the filter shall not generate significant quantities of smoke or toxic fumes into the air stream. In no case shall the total toxic vapour emission into the air stream, calculated over a period of 10 minutes, result in the 10 minute exposure level of any toxic constituent, being exceeded.
3 | Where flameproof filters are used, the frames, casings and filter cell holding frames shall be classified non-combustible.
11.3 | FILTER SECTION
A. | Air Filters: Refer to Section "Particulate Air Filters."
B. | Filters: Comply with NFPA 90A.
C. | Provide minimum arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.
D. | Filter Housing: Provide filter media holding frames arranged for flat, angular orientation, or bag filters, minimum thickness, 14 gage galvanized steel with baked finish inside and out. Joints shall be continuously welded. Flange shall have a fixed air-sealing gasket with hollow cross section, closed cell rubber or resilient neoprene, suitable for repetitive reuse. Cabinets shall have flanged ends for connection to adjacent ducts. Hinged access doors on both cabinet sides. Provide access doors with fixed air sealing gaskets to be airtight at the static pressure expected in service. Weld test ports into each filter cabinet or plenum. Test port shall not penetrate to filter frame or media.
E. | Pre-filters: 25 mm thick, viscous-coated fibers flat panel with cardboard frame and perforated metal retainer, clean airflow resistance of 62 Pa (0.25 inch wg) at face velocity of 2.54 m/s (500 fpm), and ANSI/ASHRAE 52.1 filter-arrestance efficiency of 60 to 80 percent.
F. | Permanent Filters: Bag type, viscous coated fiber, 450mm long with holding stainless steel frames and fasteners, and ASHRAE filter-arrestance efficiency of 60 to 80 percent.
G. | Construction Filters for pre-commissioning: 25 mm thick, viscous-coated fibers encased in fiberboard cell with perforated-metal media support, clean airflow resistance of 37 Pa at face velocity of 1.52 m/s and ASHRAE 52.1 filterarrestance efficiency of 70 to 82 percent.
H. | Filter Gage:
1 | 90-mm- (3-1/2-inch-) diameter, diaphragm-actuated dial in metal case.
2 | Vent valves.
3 | Black figures on white background.
4 | Front recalibration adjustment.
5 | 2 percent of full-scale accuracy.
6 | Range: 0 to 1000 Pa (0- to 4.0-inch wg).
7 | Accessories: Static-pressure tips with integral compression fittings, 6-mm (1/4-inch) plastic tubing, and 2- or 3-way vent valves.
11.4 | FILTER AND AIR CLEANER SECTION
A. | General: Provide filter sections with filter racks, minimum of one access door for filter removal, and filter block-offs to prevent air bypass.
B. | Hi-Efficiency Filters:
1. | Media: 50 mm prefilter and 600 mm closely spaced, pleated, fine fiber, hi-efficiency filter, sealed into a rigid frame, and capable of operating up to a maximum of 3.17 mps without loss of efficiency and holding capacity.
2. | Filter Rack: Side-access designed to hold rigid frames.
3. | Minimum Efficiency Reporting Value: 13 MERV when tested in accordance with ASHRAE Std 52.2.
4. | See Section 23 40 00.
C. | Differential Pressure Gauge:
1. | Provide factory installed dial type differential pressure gauge, flush mounted with casing outer wall, and fully piped to both sides of each filter to indicate status.
2. | Maintain plus/minus 1 percent accuracy within operating limits of minus 6.7 degrees C to 52 degrees C.

## 12.1 Heat Recovery
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
2.11 | HEAT RECOVERY
A. | Plate heat exchanger
1 | Plate to plate heat exchangers shall be of the diagonal flow type manufactured from separating aluminium plates with a PVC coating or stainless steel plates as indicated elsewhere.
2 | The unit shall be adequately sealed to prevent leakage or cross contamination.
3 | The exchanger shall be mounted over a stainless steel removable drain tray.
4 | Where indicated face and bypass dampers shall be fitted and shall be suitable for motorisation.
5 | The minimum thermal efficiency shall not be less than that stated elsewhere.
6 | The heat exchanger elements shall be designed to withstand the external and differential pressures without deformation.
B. | Run Around Coils
1 | Run around coils shall comply with the requirements as stated for cooling coils stated elsewhere.
2 | The AHU manufacturer shall provide a complete package consisting of pipework, circulating pump and expansion vessel.
3 | The pipework shall be arranged to provide full flow through the supply coil at all times.
4 | Pumps shall be constructed with cast iron bodies, bronze impellers and mechanical seals driven by totally enclosed or drip proof fan cooled motor suitable for single phase 230V electricity supply. An isolating valve and strainer shall be provided on the inlet and an isolating valve on the discharge.
5 | An altitude gauge and cock shall be provided on the system connection to the expansion vessel, together with a 15 mm safety valve on the pump discharge, set to discharge at a pressure of 5 bar unless indicated otherwise.
6 | The expansion vessel shall be of steel construction with internal flexible rubber diaphragm, precharged with inert gas.
7 | The system shall be complete with drain and make up valve with hose connection and vent cock.
8 | The pressurisation units shall be selected to accommodate the expansion in the system.
C. | Thermal Wheel Heat Exchanger
1 | Rotating regenerative air-to-air heat recovery units shall transfer sensible or total heat as indicated elsewhere between the exhaust and intake airstreams.
2 | The heat recovery wheels will be designed and manufactured to maximise the sensible and latent heat recovery and include a desiccant coating to ensure that the latent heat recovery obtained.
3 | The heat wheel shall include the following:-
a. | Integral purge section
b. | Casing seals on periphery of rotor, on duct divider, and on purge section
c. | Supported rotor on grease-lubricated ball bearings with extended grease fittings.
4 | Tapered roller bearing for horizontal mounting of wheels
5 | Heat wheels shall consist of a rigid mild steel casing protected against corrosion, containing a sectioned wheel composed of aluminium foil or other indicated heat exchange media, treated with a coating having the necessary hygroscopic properties where total heat extraction is specified.
6 | The coating or the heat exchange media shall not support bacteria, fungi or mould growth and shall be coated to prohibit corrosion.
7 | The media shall be easily cleanable and dry particles up to 800 microns, unless stated otherwise, shall pass freely through the media.
8 | The unit shall be provided with an adjustable purge sector designed to limit cross contamination to less than 0.04 % of the exhaust air-stream concentration. This media shall be rigidly held in place.
9 | The wheel shall be certified by an independent test laboratory for cross contamination using tracer gas SF6 or equivalent.
10 | The rotor shall be speed controlled via an inverter allowing a turn down ratio as indicated and shall be suitable for interfacing with the BMS as indicated elsewhere.
11 | Provision shall be made for adjustment of drive belt or drive chain tension.
12 | Thermal wheel heat exchangers shall have a minimum thermal efficacy of 70%.
13 | The complete wheel and motor drive shall be mounted within an air handling unit section. Access doors shall be located on each side of the heat recovery unit in the adjacent intake and exhaust ductwork.
14 | The maximum rotation speed shall be 20 rpm and maximum face velocity shall be 2.5 m/s.
15 | An integral factory mounted control panel shall be provided wired to the motor with air stream thermostat and manual motor starter for field wiring; with pilot light indication of rotor rotation and provisions for setting maximum and minimum speed.
16 | Changeover Control:- Electronic automatic summer changeover system for field mounting of room and outdoor air temperature sensors, to provide maximum rotor speed when air temperature is less than outdoor air temperature.
17 | Rotation Detection: - Electronic control module, electromagnetic sensor, and iron shuttle factory wired and mounted, with alarm bell for field wiring and mounting, and remote alarm capability.

## 13. Horse Shoe Heat Pipe
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
14.1 | Horse Shoe Heat Pipe (wrap around type)
a. | Heat pipes shall be included within the AHU and wrapped around the main cooling coil. The wrap-around heat pipes pre-cool the fresh/return air allowing more of the cooling coil surface to be utilized for the removal of moisture. The dehumidified air is then passively reheated by the heat pipe to the supply condition.
b. | Heat pipes shall comprise, a precool fin block upstream of the main cooling coil linked to a reheat fin block downstream of the cooling coil by means of ‘wrap-around’ pipes.
c. | All coils shall be provided with durable flexible epoxy polymer coating to protect the coil fins from corrosion due to salt and sand laden air. The coating process shall ensure complete coil encapsulation and have a uniform dry film thickness between 0.8 to 1.2mil on all surface areas including the fin edges. Corrosion durability shall be confirmed through testing to no less than 1000 hours salt spray per ASTM B117-90. The coil selection shall include the derating of the output due to the coating and the coating shall have a minimum 15 year guarantee.
2 | Fins
a. | The external fins shall be of aluminium with a minimum thickness of 0.15mm. Fins shall be of the continuous plate type to maximize the external surface area. The fins shall be of the louvered type to optimize the airside heat transfer and spaced at such a distance as required by the conditions specified elsewhere.
3 | Tubes
a. | Tubes shall be of refrigeration standard seamless copper C106 for heat exchanger use. Tube diameter shall be 12mm with a grooved inner surface to enhance the internal surface area and prevent pooling of liquid. The number of rows of tubes shall be selected to suit the application. Multiple row heat pipes shall have tubes in a staggered, equilateral pattern to optimize the airside heat transfer.
4 | Casing
a. | Casings shall be from galvanized sheet steel with a minimum thickness of 1.6mm. The casing shall incorporate tube plates and top and bottom plates around both the precool and reheat heat pipe blocks. Cover boxes shall be provided around the wrap-around pipes both to protect the exposed pipes and to rigidly join the two sections. Extra sheet metal shall be provided to ensure rigidity during manufacture and transport.
5 | Working Fluid
a. | The refrigerant shall be R134a and the heat pipe circuits shall be factory charged and hermetically sealed with the calculated weight of refrigerant.
6 | Circuitry
a. | Heat pipes shall be formed from an array of complete loops such that the working fluid flows around the loop in only one direction i.e. liquid and vapour flow in the same direction to ensure that returning liquid is not entrained by the vapour.
b. | There shall be a multitude of loops in the height of the heat pipe and each loop shall be individually charged. Heat pipes with header assemblies containing a single circuit are not suitable as a single leak will render the entire heat pipe inoperative.
c. | When multiple row heat pipes are used the rows shall be connected together in a counter flow orientation to optimize the performance of the heat pipe. Rows shall not be manifolded together.
d. | Heat pipe loops shall be arranged to slope down to the precool side to allow gravity assisted liquid return to maximize the internal heat transfer.
7 | Performance
a. | Heat pipes shall be designed to comply with the specified conditions when subject to the air volumes given in the specification. Heat pipe performance shall be independently type tested and certified in line with the requirements of British Standards BS 5141 pt1 / European Standards EN 305 & 306 / American Standards ARI 410 for testing and rating of heat exchangers. All software used to predict the performance of heat pipes shall be based upon the results of these independent tests.
8 | Installation
a. | The heat pipe shall be designed to fit around the main cooling coil and its dimensions shall be selected so as to allow this. Once installed within the AHU both the heat pipe and cooling coil shall be blanked-off to ensure that there is no air bypass around the fin blocks of either the heat pipe or cooling coil. A drip tray shall be provided below the heat pipe/cooling coil as specified elsewhere.
9 | Independent Test Report
a. | The heat pipe should have a third party independent test report conducted by a certified laboratory.
10 | Manufacturing Experience
a. | The heat pipe manufacturer shall have a minimum of 10 years’ experience in manufacturing of heat pipes and must have heat pipes commissioned for a minimum period of 5 years.
11 | Selection Criteria
a. | The number of rows and fins spacing shall be selected to achieve the most optimum performance of heat pipe throughout the year, based on the design criteria stated elsewhere.

## 14. Coils
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
14.1 | COILS
A. | Coils shall be selected and located to ensure the full design air flow is evenly dispersed across the full coil face area.
B. | Coil design and sizing shall be based on figures obtained from performance tests described in BS 5141 for cooling and heating coils.
C. | Coils shall be guaranteed to meet the specified performance. All coils shall be tested before leaving the manufacturer's works. An independently witnessed test certificate shall be issued to the CA for each coil. Each coil shall be indelibly marked with the details of the test.
D. | Unless stated otherwise elsewhere the maximum water coil pressure drop shall be as stated below;
1 | Cooling – 20Kpa
2 | Heating – 15kpa
E. | Coils shall be pressure tested at the manufacturer’s works to a minimum of 1.5 times the working pressure or 8 bar gauge pressure whichever is the greater.
F. | The flow and return battery connections shall be labelled and the air flow direction shall be indelibly marked on the battery casing.
G. | Coils shall be mounted in the unit casing so that they can be removed from the side without dismantling the entire unit.
H. | Coils with minor damage to fins shall be combed straight. Coils with extensive fin damage will not be acceptable and shall be replaced.
I. | Flow and return headers shall be arranged to ensure equal flow through all tubes. Provision shall be made for expansion and contraction of the tubes and for effective venting and draining of the coil. Each coil shall be provided with a full bore dirt pocket with drain valve on the lower connection.
J. | Coils shall be arranged in sections to facilitate removal.
K. | The tube and fin spacing shall be arranged to ensure maximum heat transfer efficiency with minimum coil depth and air resistance.
L. | Tube wall thickness and coil construction shall be suitable for the system operating pressures and temperatures.
M. | Unless stated otherwise elsewhere coils shall be manufactured from 16mm (OD) copper tube with a minimum wall thickness of 0.4mm and a 35mm pitch.
N. | Connections up to and including 50 mm diameter for water pressures up to 350 kPa shall be screwed to BS EN 10226-1. Larger sizes and connections for pressures over 350 kPa shall be flanged to BS EN 1092. Connections shall be clear of coil casings with disconnection joints positioned to permit full withdrawal and removal of coils without extensive dismantling of adjacent pipework, ductwork or other equipment.
O. | Coils shall be mounted in a mild steel framed casing having a minimum thickness of 1.2 mm. Casings shall be hot dip galvanised in accordance with BS EN ISO 1461 after manufacture. The casing shall be of adequate strength for the size of the coil.
P. | Coils shall comprise solid drawn seamless copper tubes unless otherwise stated. Copper tube shall comply with BS EN 12451 and have suitable wall thickness for the pressure application. Headers shall be either copper or steel as stated elsewhere.
Q. | Fins shall make firm and continuous contact with the primary tubes and be constructed from aluminium or copper as stated elsewhere and have a minimum thickness of 0.15mm. Fins shall be of the “rippled or louvered” type to suit the air flow requirements and be spaced at distance to suit the specified performance of the coils.
R. | Where coil connections pass through the casing they shall be complete with sealing rings and removable plates.
S. | Unless otherwise indicated each coil shall be provided with a self-sealing combined pressure and temperature test point on the flow and return. All coils shall include an air vent and drain plug.
T. | Coils shall be of the cartridge type.
U. | Access Panel:
1 | Removable panels shall be assembled at coil section casing walls.
2 | Panels shall be bolted externally for air-tightness, easy removal and quick reassembly to facilitate access for servicing and maintenance.
14.2 | Chilled Water
1 | Cooling coil face velocities shall not exceed 2.0 m/s and the resistance to airflow shall not exceed 125Pa unless otherwise indicated.
2 | The air velocity across the coil shall be such that free water shall not be carried over from the coil to the air-stream.
3 | Unless otherwise indicated coils shall be constructed from copper tubes with continuous aluminium fins pressure bonded to the tubes through mechanical expansion and all housed in stainless steel frames. Fins shall have solid drawn spacing collars.
4 | All coils shall be provided with durable flexible epoxy polymer coating to protect the coil fins from corrosion due to salt and sand laden air. The coating process shall ensure complete coil encapsulation and have a uniform dry film thickness between 0.8 to 1.2mil on all surface areas including the fin edges. Corrosion durability shall be confirmed through testing to no less than 1000 hours salt spray per ASTM B117-90. The coil selection shall include the de-rating of the output due to the coating and the coating shall have a minimum 15 year guarantee.
5 | Cooling coil casings shall incorporate an insulated watertight drain tray complete with drain connection. Trays and drains shall be arranged with longitudinal and cross gradients to ensure total removal of all condensate. Drain trays shall be insulated from the factory with 12 mm thick closed cell elastomeric foam rubber insulation
6 | Unless otherwise indicated drain trays shall be fabricated from AISI 316 stainless steel of minimum 1mm thickness and be provided with a threaded drain outlet. The condensate drain pipe connection through the unit casing shall be insulated from the factory with 12 mm thick closed cell elastomeric foam rubber insulation and sealed with plastic grommet.
7 | Large coils constructed in two horizontal sections they shall have separate connections/headers and shall be assembled correctly to ensure that the top section condensate flows evenly onto the lower section. Where this is not possible a separate condensate baffle/catch plate shall be installed with a separate drain to the coil drain pan.
8 | Unless otherwise indicated, PVC eliminator blades retained in galvanised steel plate shall be provided after each coil and shall be located such that any carry over will collect and fall into the drain pan. Eliminator sections shall be positioned to avoid damage from adjacent heater batteries and shall be of materials unaffected by such heat. An access door shall be provided between the coil and eliminator plates.
14.3 | Heating Coils
1 | Heating coil face velocities shall not exceed 3 m/s and the resistance to airflow shall not exceed 65Pa unless otherwise indicated.
2 | Unless otherwise indicated, heat transfer surfaces shall consist of multiple seamless copper tubes with extended surface of aluminium fin plates having solid drawn collars through which the tubes pass.
3 | All coils shall be provided with durable flexible epoxy polymer coating to protect the coil fins from corrosion due to salt and sand laden air. The coating process shall ensure complete coil encapsulation and have a uniform dry film thickness between 0.8 to 1.2mil on all surface areas including the fin edges. Corrosion durability shall be confirmed through testing to no less than 1000 hours salt spray per ASTM B117-90. The coil selection shall include the de-rating of the output due to the coating and the coating shall have a minimum 15 year guarantee.
4 | The assembled fin blocks shall be supported with galvanised sheet steel framing, having end plates with accurately formed collars for tube support, allowing tube movement during expansion and contraction without abrasion or chafing. The fin block tubes shall be extended and brazed into seamless copper headers.
5 | Flow and return headers shall be arranged so as to provide reverse return water flow and with the return header at the air inlet face of the coil. Return bends shall be of copper of the same diameter as the tubes and shall be brazed into the expanded fin block tube ends.
6 | Large coils shall be split horizontally for ease of handling and installation.
7 | Coil blocks shall be insulated and fitted with removable galvanised sheet steel metal enclosures.
14.4 | Cooling Coils - Direct Expansion
1 | Unless otherwise indicated coils shall be constructed from continuous aluminium/plate fins, mechanically bonded to seamless refrigerant quality copper tubes.
2 | All coils shall be provided with durable flexible epoxy polymer coating to protect the coil fins from corrosion due to salt and sand laden air. The coating process shall ensure complete coil encapsulation and have a uniform dry film thickness between 0.8 to 1.2mil on all surface areas including the fin edges. Corrosion durability shall be confirmed through testing to no less than 1000 hours salt spray per ASTM B117-90. The coil selection shall include the de-rating of the output due to the coating and the coating shall have a minimum 15 year guarantee.
3 | The tube and fin spacing shall be arranged to ensure maximum heat transfer efficiency with minimum coil depth and air resistance.
4 | Direct-expansion refrigerant cooler coil materials shall be selected to minimise electrolytic action.
5 | Coils shall be mounted in the unit casing so that they can be removed from the side without dismantling the entire unit.
6 | Refrigerant circuitry shall be designed to ensure equal distribution of refrigeration to each circuit across the whole face of the coil.
7 | Return or suction connections shall be arranged to ensure complete drainage of oil in the evaporator.
8 | The design of the refrigerant passages in direct expansion type evaporators shall be such that any oil present is always carried back to the compressor at the lowest stage of capacity reduction.
9 | The complete evaporator coil shall be pressure tested at the manufacturer’s works to twice the working pressure. After testing, the coils shall be dehydrated under vacuum and charged with nitrogen before sealing.
10 | Coil face velocity shall not exceed 2.0 m/s unless stated otherwise elsewhere.
11 | Evaporator and refrigeration shall be compatible with regard to duty and capacity control.
12 | Evaporators shall be dehydrated and charged with an inert gas and sealed after manufacture.
13 | Cooling coil casings shall incorporate an insulated watertight drain tray complete with drain connection. Trays and drains shall be arranged with longitudinal and cross gradients to ensure total removal of all condensate. Drain trays shall be insulated from the factory with 12 mm thick closed cell elastomeric foam rubber insulation
14 | Unless otherwise indicated drain trays shall be fabricated from AISI 316 stainless steel of minimum 1mm thickness and be provided with a threaded drain outlet. The condensate drain pipe connection through the unit casing shall be insulated from the factory with 12 mm thick closed cell elastomeric foam rubber insulation and sealed with plastic grommet.
15 | Intermediate drain trays shall be provided where the coil height exceeds 1metre and for each additional 1metre of coil height.
16 | On large coils constructed in two horizontal sections they shall have separate connections headers and shall be assembled correctly to ensure that the top section condensate flows evenly onto the lower section. Where this is not possible a separate condensate baffle/catch plate shall be installed with a separate condensate baffle/catch plate shall be installed with a separate drain to the coil drain pan.
17 | Unless otherwise indicated, PVC eliminator blades retained in galvanised steel plate shall be provided after each coil and shall be located such that any carry over will collect and fall into the drain pan. Eliminator sections shall be positioned to avoid damage from adjacent heater batteries and shall be of materials unaffected by such heat. An access door shall be provided between the coil and eliminator plates.
18 | Where coil connections pass through the casing they shall be complete with sealing rings and removable plates.
14.5 | CONDENSATE DRAIN PANS
A. | Provide condensate drains to all cooling coils, humidifier sections and recuperator sections of the air handling units.
B. | Condensate drains shall be run in a safe manner to discharge over an appropriate gully or to a sump as indicated.
C. | Connections shall be made by the Contractor, with glass "U" traps having a water seal depth of not less than twice the fan static pressure, together with a tapping for maintaining the water seal. Where necessary the trap shall be protected against accidental damage.
D. | The drains shall discharge into a tundish.
E. | Drains on pans under negative pressure are to have the outlet positioned low enough to prevent condensation being held in the drip tray.
F. | Where drains have to run across a walkway the Contractor shall provide a permanent step over. Where possible this should be avoided.
G. | Drains shall comply with recommendations in CIBSE Technical Memorandum TM13 and HSE L8.
14.6 | COOLING COILS
A. | Coils shall be selected and located to ensure the full design air flow is evenly dispersed across the full coil face area.
B. | Coil design and sizing shall be based on figures obtained from performance tests described in BS 5141 for cooling and heating coils.
C. | To combat the area acid and salt atmospheric conditions the unit cooling coils assemblies shall protected against corrosion. The coils shall have a warranty of 10 years against corrosion. Acceptable methods of protection are as follows:
1 | Copper Coils, Copper Fins: Electro-tinned
2 | Copper Coils, Copper Fins: Factory Applied Heresite
3 | Copper Coils, Copper Fins: Factory Applied Bly-Gold
4 | Copper Coils, Aluminum Fins: Factory Applied Heresite
5 | Copper Coils, Aluminum Fins: Factory Applied Bly-Gold
D. | Watertight drain trays shall be provided and fabricated from stainless steel.
E. | Intermediate drain trays shall be provided where the coil height exceeds 950mm. The general arrangement shall ensure that collected water is drained towards one end of the tray and through the lowest point in the tray to the lower tray, via a down pipe, without splashing. Further drain trays shall be provided for each additional 950mm of coil height.
F. | Eliminator sections shall be positioned to avoid damage from adjacent heating coils and shall be of materials unaffected by such heat.
G. | Coils shall be arranged to provide equal fluid flow through all coil circuits. Multi-row coils shall be arranged in contra flow with the water entering at the air leaving end and leaving at the air entering end. The flow and return coil connections shall be labelled and the air flow direction shall be indelibly marked on the coil casing. Coils shall be eight rows maximum depth.
H. | Heat exchanger finned surfaces shall extend for the full width of the coil casing except where baffles, suitably protected against corrosion, are provided to prevent air by-passing the finned surface. Sealing devices shall be fitted to top and bottom of coils to prevent air by-pass and water carry-over.
Fins shall make firm and continuous contact with the primary tubes. Where more than one primary tube is required, tube rows shall be staggered in the direction of air flow to maximise heat transfer and provide even air distribution across the face of the coils.
J. | The completed battery shall be tested to 210kPA air under water after manufacture and shall be hydraulically tested and certified to 21 bar.
K. | Batteries mounted in ductwork shall be supported so that the ductwork does not take the weight.
L. | Chilled water cooling coils and access sections shall be lined with polished 304 stainless steel with manually operated isolating dampers on the access sections. Isolation dampers shall be tight shut off type construction with polished 304 stainless steel and the cooling coil shall be constructed with copper tube and copper fins electro-tinned after manufacture. The cooling coil section must have an easily removable and oversized polished 304 stainless steel drain trays. The drain tray serving the cooler shall be extended or a separate tray shall be provided to collect water from the eliminator. Drain trays shall be sloped to fall (1 in 20) towards a flush drain connection so that no water is retained in the drain tray. A pipework drain connection, complete with quick-release refillable trap, shall be extended from the lowest point on the underside of the tray to the nearest sump or gully to discharge through an air break. A water seal of sufficient depth shall be provided to prevent entry or exit of air to or from the system and additionally maintain a 75mm seal when the plant is de-energised. The distance between the underside of the tray and the crown of its trap is to be sufficient to ensure the tray is fully drained during operating periods.
M. | The coils shall be easily removable to facilitate regular cleaning and the limiting of legionella growth risk.
N. | On large coils constructed in two horizontal sections they shall have separate connections headers and shall be assembled correctly to ensure that the top section condensate flows evenly onto the lower section. Where this is not possible a separate condensate baffle/catch plate shall be installed with a separate condensate baffle/catch plate shall be installed with a separate drain to the coil drain pan.
O. | Face velocities across the cooling coil shall not exceed 2.25 metres per second and the maximum pressure drop across the cooling coils shall not exceed 100 Pa (air side) and 30kPa (water side). The cooling coil shall be fabricated from a stainless steel casing and mounted on slide tracks for future coil removal.
P. | Header connections on CHW cooling coils shall be screwed to up to and including DN 50 and flanged for DN 65 and above.
Q. | Screwed connections shall be made using ground-in spherical seated unions.
R. | Water coils shall have a means of venting and draining.
S. | Isolating valves shall be provided on the inlet and outlet connections arranged to facilitate removal of the coil. Steam coils shall have an air release tapping.
T. | Accessible temperature sensor pockets shall be provided to all flow and return headers for monitoring purposes.
U. | Water coils shall have self-sealing test points on the inlet and outlet connections to each water coil.
V. | Coils shall be supported so that their weight is not transmitted to ductwork or pipework and so that removal can be achieved without disturbing adjacent ductwork and other services.
W. | Minor damage to fins shall be rectified by combing. Coils with extensively damaged fins shall be replaced where damage results in an increase in pressure drop of greater than 10% of the design value.
X. | Coils shall be tested before leaving the manufacturer's works. A test certificate shall be provided for each coil.
Y. | Each water coil shall be tested for leaks by using air under water to 1.5 times the working pressure or 8 bar gauge pressure, whichever is greater, for 30 minutes.
Z. | Each steam heating coil shall be hot soaked for 1 hour followed by live steam purged for 30 minutes at a minimum pressure of 140 mbar gauge and then tested for leaks by using air under water as for water coils.
AA. | Each direction-expansion refrigerant cooling coil shall be tested for leaks by using air under water to 19 bar gauge pressure for 30 minutes.
14.6 | CONDENSATE DRAINS
A. | Provide condensate drains to all cooling coils, humidifier sections and recuperator sections of the air handling units.
B. | Condensate drains shall be run in a safe manner to discharge over an appropriate gully or to a sump as indicated.
C. | Connections shall be made by the installer, with glass "U" traps having a water seal depth of not less than twice the fan static pressure, together with a tapping for maintaining the water seal. Where necessary the trap shall be protected against accidental damage.
D. | The drains shall discharge into a copper turndish.
E. | Drains on pans under negative pressure are to have the outlet positioned low enough to prevent condensation being held in the drip tray.
F. | Where drains have to run across a walkway the installer shall provide a permanent step over.
G. | Drains shall comply with recommendations in CIBSE Technical Memorandum TM13 and HSE L8 in connection with Legionnaires' disease.
14.7 | COILS
A. | Coil Sections: Common or individual, insulated, galvanized steel casings for heating and cooling coils. Design and construct to facilitate removal and replacement of coil for maintenance and to assure full airflow through coils.
1. | Multizone Units: Provide air deflectors and air baffles to balance airflow across coils.
B. | Coil Construction: Rigidly supported across full face, pitched to allow drainage.
1 | Fins: Aluminum, mechanically bonded to tubes.
2 | Tubes: Seamless copper, minimum thickness: 0.035 inches. .(Coil thickness can be reduced subject to certification from manufacturer regarding coil suitability for actual working pressure).
3 | Coil Casing: Galvanized steel.
4 | Headers for Steam and Water Coils: Steel, cast iron, or copper with connections for drain valve and air vent, and threaded piping connections.
C. | Water Coils: Drainable with threaded plugs, serpentine with return bends in smaller sizes and with return headers in larger sizes.
D. | Coil face area velocity is not to exceed 2.5 meters per second at specified air quantity. Coil to have number of rows and fins per cm to satisfy required capacity at specified condition, with not more than 5 fins per cm.
E. | Number of circuits to be such that water velocity satisfies specified conditions without exceeding specified maximum water pressure drop through coil. Water velocity through tubes is not to exceed 1.8 meters per second and not less than 0.76 meters per second.
F. | Steam Coils: Steam-distributing type with concentrically supported distributing tube.
G. | Direct-Expansion Refrigerant Coils: ASHRAE 15 AND 34 PACKAGE, with the following features:
1 | Suction Headers and Distributor Tubes: Seamless copper.
2 | Refrigerant Distributor: Design for low pressure drop, for down feed with solder connections, and with maximum of 12 circuits for each distributor.
H. | Electric-Resistance Coils: Open-wire type, 80 percent nickel, 20 percent chromium elements, uniformly distributed and supported in aluminized- or galvanized steel frame with vertical support brackets and insulated with ceramic bushings.
I. | Electric-Resistance Coils: Finned-tube construction with 80 percent nickel, 20 percent chromium elements, mounted in copper-plated steel tube and surrounded by magnesium-oxide powder; spirally wound with copper-plated steel fins brazed to tubes; mounted in aluminized- or galvanized steel frame.
1 | Control Panel: NEMA 250, Type 1 enclosure, with thermal cutouts, primary and secondary controls, back-up contactors, circuit fusing, airflow switch, and fused control transformer. Include integral primary automatic and secondary manual reset thermal-protection devices and airflow switches.
2 | Controls: Refer to Section "Building Management System."
J. | Coil-Performance Tests: Factory-test cooling and heating coils, except sprayed surface coils for rating according to ANSI/AHRI 410, "Forced-Circulation AirCooling and Air-Heating Coils."
14.8 | COIL SECTION
A. | Casing: Provide access to one side of coils. Enclose coils with headers and return bends fully contained within casing. Slide coils into casing through removable end panel with blank off sheets and sealing collars at connection penetrations.
B. | Drain Pans: 600 mm downstream of coil and down spouts for cooling coil banks more than one coil high.
C. | Air Coils:
1. | Certify capacities, pressure drops, and selection procedures in accordance with AHRI 410
D. | Fabrication:
1. | Tubes: 16 mm OD seamless copper expanded into fins, brazed joints comply with middle east standard.
2. | Fins: Aluminum.
3. | Casing: Die formed channel frame of galvanized steel.
E. | Water Cooling Coils:
1. | Headers: Cast iron, seamless copper tube, or prime coated steel pipe with brazed joints.
2. | Configuration: Drainable, with threaded plugs for drain and vent; threaded plugs in return bends and in headers opposite each tube.
F. | Drain Pan Construction:
1. | Provide cooling coil and humidifier sections with an insulated, double wall, stainless steel drain pan complying with ASHRAE Std 62.1 for indoor air quality and sufficiently sized to collect all condensate.
2. | Slope in two planes to promote positive drainage and eliminate stagnate water conditions.
3. | Locate outlet of sufficient diameter at lowest point of pan to prevent overflow at normal operating conditions.
4. | Provide threaded drain connections constructed of drain pan material, extended sufficient distance beyond the base to accommodate field installed, condensate drain trapping.
J. | Louvers: Stationary, of galvanized steel, 100 mm deep with plenum, nylon bearings, 13 mm mesh, 1.0 mm galvanized wire bird screen in aluminum frame, and bearing AMCA
Certified Ratings Seal in accordance with AMCA 500-L. Furnish adjustable louvers with hollow vinyl bulb edging on blades and foam side stops to limit leakage to maximum 2 percent at 1 kPa differential pressure when sized for 10 m/s face velocity.

## Drain Pan Details
Drain pan |  |  | Sr | Specifications | UAE Factory | KSA Factory
Drain pan Construction-General | Drain pan will be made of 1.5 mm thick stainless steel, adequatly sized to collect condensate from cooling coils (including coil piping connections and return bends) and multi-sloped to ensures positive drainage. Drain pan is under side lined with 15 mm thick Aluminum foil faced XLPE insulation. Drain pan will be placed on double skin insulated bottom or floor panels. The drain pan connection is located at the lowest point of the drain pan and shall be of sufficient diameter to drain freely. Drain pan is highest level of accessibility for periodic cleaning. Drain pan shall have necessary slope to facilitate fast removal of condensate and arrangement to be provided to slide the coil. Condensate drain pan under cooling coils shall be insulated single skin stainless steel construction. Drain pan is placed on 42/62 mm thick double skin insulated bottom panel and additionally bottom of the drain pan is lined with 15 mm thick Aluminum foil faced XLPE insulation. |  |  | Drain Pan Details
| Drain pan is made of Stainless steel and placed on double skin insulated bottom panel and additionally bottom of the drain pan is lined with 15 mm thick Aluminum foil faced XLPE insulation. Drain pan is adequately sized to collect condensate from cooling coils (including coil piping connections and return bends) and multi-sloped to ensures positive drainage. |  | 14.1 | COILS
| Construct drain pans water tight, treated to prevent corrosion, and designed for positive condensate drainage. When 2 or more cooling coils are used, with one stacked above the other, condensate from the upper coils shall not flow across the face of lower coils. Provide intermediate drain pans or condensate collection channels and downspouts, as required to carry condensate to the unit drain pan out of the air stream and without moisture carryover. Construct drain pan to allow for easy visual inspection, including underneath the coil without removal of the coil and to allow complete and easy physical cleaning of the pan underneath the coil without removal of the coil. Coils shall be individually removable from the casing. |  | A. | Coils shall be selected and located to ensure the full design air flow is evenly dispersed across the full coil face area.
ASHRAE 62.1 Compliance-Drain pan | ASHRAE 62.1 Compliance-Drain pan Requirements 5.10 Drain Pans. Drain pans, including their outlets and seals, shall be designed and constructed in accordance with this section. 5.10.1 Drain Pan Slope. Pans intended to collect and drain liquid water shall be sloped at least 0.125 in./ft (10 mm/m) from the horizontal toward the drain outlet or shall be otherwise designed to ensure that water drains freely from the pan whether the fan is on or off. 5.10.2 Drain Outlet. The drain pan outlet shall be located at the lowest point(s) of the drain pan and shall be of sufficient diameter to preclude drain pan overflow under any normally expected operating condition. 5.10.3 Drain Seal. For configurations that result in negative static pressure at the drain pan relative to the drain outlet (such as a draw-through unit), the drain line shall include a Ptrap or other sealing device designed to maintain a seal against ingestion of ambient air while allowing complete drainage of the drain pan under any normally expected operating condition, whether the fan is on or off. 5.10.4 Pan Size. The drain pan shall be located under the water-producing device. Drain pan width shall be sufficient to collect water droplets across the entire width of the water-producing device or assembly. For horizontal airflow configurations, the drain pan length shall begin at the leading face or edge of the water-producing device or assembly and extend downstream from the leaving face or edge to a distance of either a. one half of the installed vertical dimension of the waterproducing device or assembly or b. as necessary to limit water droplet carryover beyond the drain pan to 0.0044 oz/ ft2 (1.5 mL/m2) of face area per hour under peak sensible and peak dew-point design conditions, considering both latent load and coil face velocity.
Drain pan Construction-Detailed
Material and thickness | Standard material is 1.5 mm thick made of GI (we need to check with Mr. Azeem for coating), Coating will be plain powder coating (similar to unit outer skin coating). Coating will be plain whereas for outer skin it will be texture. | Not applicable for Saudi
Optional SS304, SS316.
Drain pan made of corrosion resistant powder coated Galvanized steel.
Construction | The Drain pan offered should be fabricated of galvanized steel sheet protected with powder coating paint. Beneath the drain pan, it should be covered with 10mm PE insulation to prevent any occurrence of condensation
Drain pan shall have a threaded, extended pipe connection, sealed to the unit casing with heavy duty PVC gasket terminating outside of the unit
Drain pan sloped | Standard drain pan will be 3 sloped type (ie, sloped on x & y Axis), under side lined with 15 mm thick Aluminum foil faced PU elastic insulation.
Horizontal supports are welded (material same as drain pan) to drain pan.
Drain pan, Horizontal supports, L channels will be min 1.5 mm thick
Drain pan size | Drain pan extends after coil approximately by 200 mm
1. Drain pan length is 150 mm longer after the coil. We can comply with ASHRAE 62.1 with extended drain pan with an ADDITIONAL COST.
Extended drain pan | Extended drain pan need to be selected even is drip eliminator is there.
| Due to proper collection of condensate, we need to give extended drain pan for FAHU. No need for AHU. | Irfan
| Due to proper collection of condensate, Above 1.5 m height coil, give extended drain pan | Azeem
Depth | Drain pan height one side is fixed to 40mm other side will be vary based on unit width and slop | Ghouse
Upstream & down stream extension of drain pan.
Connection type | Connection will be threaded, material same as drain pan, welded to drain pan provided on middle, side of drain pan.
Drain connection size | If Unit width less then 1.5 meter 1" standard same as Italy unit width above 1.5 meter 1 1/2" adding this from local factory otherwise as ASTRA standard all the sizes 1"
From bottom height of drain connection size.
Condensate drain shall be a minimum DN30 (1-1/4") diameter stainless steel tube extending 25mm (1") out from unit for solder connection to trap. Drain pans shall be installed below the entire cooling coil section and be sloped within unit and fully drainable.
The condensate drain pipe connection through the unit casing shall be insulated from the factory with 2 mm thick closed cell elastomeric foam rubber insulation and sealed with plastic grommet
Connection side | As standard, drain connections will be provided same side as coil connections. Upon request opposite side also possible.
Since drain pan is sloped, drain connection will be provided on one side only. Both side is not possible
Intermidiate Drain pan | Upper coil don't have frame on bottom side, Lower coil don't have frame on upper side. Coils are placed one above another. Intermidiate drain pan is not possible. Software will select automatically stack coils. No need to select vertical split.
Drain pan installation on floor panel | Drain pan will be placed and screwed to the double skin insulated bottom panels
Drain tray must be of withdrawable
Drain pan integrated into the floor panel | Integrated drain pan is possible, we need base frame also.
Drain pan cleaning | Drain pan shall allow visual inspection and phisical cleaning on 100% of the pan space w/o removal of coil. Provide the min 30 mm maintenance clearence b/w the drain pan and any coil casing.
Coil installation on drain pan | Cooling coils will be placed on Horizontal supports.
L-Channels (material same as coil frame) will be screwed on horizontal supports to guide the cooling coil
CHW Coils
Tube | Tube wall thickness and coil construction shall be suitable for the system operating pressures and temperatures
Fins
Header
Connection | Connections - Same end, counterflow, with vent, drain, supply and return stubs extended to outside of unit casing with grommets for airtight casing
6. If steel pipe connections are provided they shall be welded to the copper headers with silica-bronze weld to prevent dielectric corrosion of dissimilar metals and extend the life of the coils.
Frame
Coil remove | Removable coil access panels shall be provided to remove coils through casing wall. All coils shall be mounted on runners so that they can be removed easily to the access side and through the unit casing. Coil covers shall be double wall construction with all exposed edges of insulation covered with sheet metal including holes through the cover for coil header stub outs, the joint passages through these panels for connection of pipework must have airtight seals
For large capacity units (above 3,000 l/s), or where adequate coil removal space is not available based on OAHU position shown on the drawings the Contractor shall coordinate with the Engineer and allow for split coils within the AHU for ease of future maintenance and replacement.
Drain & airvent
Drip Eliminator
Condensate drift eliminators if there is a risk of water droplets carry over and not running down the fins into the drip tray.
Stack coil
Split coil
LTHW Coils
Run Around coils
Dx & Condensing coils

## 15. UV Lamps
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
15.1 | UV Lamps

## 16. Heaters
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
2.7 | Heater
1 | Electrical heater batteries shall consist of a number of heating elements of the enclosed type mounted in a sheet steel casing. Elements shall be so arranged to permit removal without dismantling
2 | Unless otherwise indicated the resistance to the air flow through the battery shall not exceed 25 Pa and the face velocity shall not exceed 6m/s nor be less than 2m/s.
3 | An isolator and a hazard warning sign clearly indicating the operating voltage shall be fitted immediately adjacent to the heater access opening.
4 | In the proximity of hot areas, the electrical wiring insulation shall be suitable for the maximum temperature.
5 | The connections from each element shall be extended to a terminal box housed in an accessible position with conduit/cable entry provision. They will be secured to the terminal box with air tight glands and will be linked with either copper bus-bars or terminals as necessary to achieve step control requirements stated elsewhere.
6 | The number of elements in the heater shall be the same as or a multiple of the number of steps in the controller. All heaters and heater sections of more than 3kW loading shall be balanced over three phases and the complete heater bank shall be arranged for balanced operation on a threephase, four-wire system.
7 | The elements shall be equally spaced over the open duct area.
8 | The whole unit will be housed in a casing manufactured to the same dimensions as the air handling unit.
9 | Each electrical heater battery shall be complete with a manually reset thermal cut-out that provides an audible or visual alarm signal on high temperature as indicated elsewhere.
10 | Unless otherwise indicated, the control of electrical heater batteries, except for remote boosters, shall be interlocked with the system fan motor starter and an air flow sensing device to ensure that the heater operates only when the fan is running and air flow is established.
11 | Electrical heater batteries which are installed as boosters in branch ducts shall each have a local air flow sensing device to ensure that the heater operates when air flow is established.
2.7 | ELECTRIC HEATER BATTERIES
A. | Electrical heater batteries shall consist of a number of heating elements of the enclosed type mounted in a sheet steel casing. Elements shall be so arranged to permit removal without dismantling
B. | Unless otherwise indicated the resistance to the air flow through the battery shall not exceed 25 Pa and the face velocity shall not exceed 6m/s nor be less than 2m/s.
C. | An isolator and a hazard warning sign clearly indicating the operating voltage shall be fitted immediately adjacent to the heater access opening.
D. | In the proximity of hot areas, the electrical wiring insulation shall be suitable for the maximum temperature.
E. | The connections from each element shall be extended to a terminal box housed in an accessible position with conduit/cable entry provision. They will be secured to the terminal box with air tight glands and will be linked with either copper busbars or terminals as necessary to achieve step control requirements stated elsewhere.
F. | The number of elements in the heater shall be the same as or a multiple of the number of steps in the controller. All heaters and heater sections of more than 3kW loading shall be balanced over three phases and the complete heater bank shall be arranged for balanced operation on a three-phase, four-wire system.
G. | The elements shall be equally spaced over the open duct area.
H. | The whole unit will be housed in a casing manufactured to the same dimensions as the air handling unit.
Each electrical heater battery shall be complete with a manually reset thermal cut that provides an audible or visual alarm signal on high temperature cut-out as indicated elsewhere.
J. | Unless otherwise indicated, the control of electrical heater batteries, except for remote boosters, shall be interlocked with the system fan motor starter and an air flow sensing device to ensure that the heater operates only when the fan is running and air flow is established. Capacity control shall be via thyristor.
K. | Electrical heater batteries which are installed as boosters in branch ducts shall each have a local air flow sensing device to ensure that the heater operates when air flow is established.

## 17. Humidifiers
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
17.1 | HUMIDIFIERS
A. | Steam Humidifiers
1 | Humidification shall be achieved by the use of dry sterile steam generated by an automatic steam humidifier selected to meet the duties as stated elsewhere. For the avoidance of doubt the humidifier shall be selected to meet the final commissioned duty of the AHU inclusive of any use of the 10% additional spare capacity of the fan duty described elsewhere in this specification.
2 | Distributor pipes shall be positioned to ensure equal mixing across the airway. In no circumstances shall the distributor pipes be less than 75% of the width of the airway and shall be designed for the air handling unit section in which they are installed.
3 | Injection pipes for introduction of dry steam from the unit into the air-stream shall be fabricated in stainless steel.
4 | The manufacturer’s recommendations regarding unobstructed space downstream of the humidifier shall be adhered to.
5 | Unless otherwise indicated, the control of humidifying plant shall be interlocked with the system fan motor starter and a local air flow sensing device to ensure that the humidifying plant operates only when the fan is running and full air flow in the humidifying section is established.
6 | The unit shall be arranged to fail safe on interruption of the water or electrical supply.
7 | Unless otherwise indicated the unit shall be supplied with a fully modulating control system operating between 10% and 100%. Below 10% output shall be on-off only.
8 | The unit shall be supplied with a control system which provides compatibility with the overall control system. Provision for remote indication shall be provided to the main control panel or BMS as indicated.
9 | Packaged electric generator units shall be contained in sheet metal stove enamelled cabinets for wall or floor mounting. Cabinets shall be provided as two separate compartments, one containing the boiler and the other the controls. Casings shall be insulated as necessary to prevent accidental contact with hot surfaces
10 | Casings shall be provided with lockable front access doors permitting full access to either compartment. Sufficient ventilation shall be provided to prevent overheating
11 | Drainage, including unit drains, shall be arranged to discharge safely and incorporate an air break.
12 | The unit shall be the electrode boiler type steam humidifier complete with stainless steel steam distributor pipes within the humidifier section of the air handling unit. The electrode shall be accessible for cleaning and not to be the disposable type.
13 | The boilers outlet shall be connected by steam hoses up to 2 m in length to steam distributor pipes in the AHU.
14 | The unit shall be designed for connection to a standard water supply with no necessary water treatment.
15 | The unit shall have the following connections:
a. | Steam outlet pipe(s)
b. | Cold water connection with solenoid feed valve and strainer
c. | Drain connection with solenoid drain/blow-down valve cited with manual override, installed into manifold and to building by others
16 | A suitable sized cold water supply shall be connected to the unit which shall comply with the Water Supply Regulations.
17 | The humidifier shall be complete with disposable scale collection bag and shall have impulse flushing to minimise sludge build-up.
18 | Steam injection pipes/hoses shall be thermal insulated where installed outside of the ductwork or air handling units.
19 | The units shall be suitable for connecting to a 3 phase and neutral electrical supply. Unit terminals shall be shrouded.
20 | The control board shall have facility for remote indication including "change of scale collector bag".
B. | Adiabatic humidifiers
1 | The humidifier shall be selected to meet the duties as stated elsewhere.
2 | For the avoidance of doubt the humidifier shall be selected to meet the final commissioned duty of the AHU inclusive of any use of the additional spare capacity of the fan duty described elsewhere in this specification.
3 | The installation and humidifiers shall comply with:
a. | Water Bylaws Scheme and must be WRAS approved.
b. | European CE Directives
c. | Health & Safety hygiene standards including the CIBSE TM 13 and EN 13779:200
4 | The water supply and distribution system must be designed, assembled and operated with regard to the risk of legionella and comply with HSE standards.
5 | The humidifier shall be capable of modulating and controlling the humidity to ±2%rRH subject to temperature control.
6 | Distributor pipes shall be positioned to ensure equal mixing across the airway. In no circumstances shall the distributor pipes be less than 75% of the width of the airway and shall be designed for the air handling unit section in which they are installed.
7 | The manufacturer’s recommendations regarding unobstructed space downstream of the humidifier shall be adhered to.
8 | Unless otherwise indicated, the control of humidifying plant shall be interlocked with the system fan motor starter and a local air flow sensing device to ensure that the humidifying plant operates only when the fan is running and full air flow in the humidifying section is established.
9 | The unit shall be arranged to fail safe on interruption of the water or electrical supply.
10 | Unless otherwise indicated the unit shall be supplied with a fully modulating control system operating between 10% and 100%. Below 10% output shall be on-off only.
11 | The unit shall be supplied with a control system which provides compatibility with the overall control system. Provision for remote indication shall be provided to the main control panel or BMS as indicated.
12 | Manifold shall be a factory assembled units consisting of air and water piping and atomising heads. The nozzles shall be fully assembled on stainless steel manifolds with compressed air blow down and pre-commissioned.
13 | The nozzle shall be robustly constructed for a long service life and guaranteed for 10 years operation and be guaranteed to be drip free atomisation.
14 | The nozzle shall be constructed from solid brass and plated with polished chrome to resist corrosion, allow easy cleaning and not support microbial growth.
15 | The humidifier system shall be designed and constructed from non-corrosive materials for hygienic operation with accessibility for easy dismantling and cleaning.
16 | At start up the humidifier system shall automatically purge the supply water line direct to drain to ensure a clean, fresh cold water supply is used for humidification.
17 | At shutdown the air shall automatically ‘run-on’ to ensure all nozzles are fully purged of water and the humidifier shall automatically drain whenever not in operation.
18 | During periods of low use or no humidity demand the system shall automatically run flush cycles to prevent water stagnation. Timings and frequency shall be programmable for optimum water consumption and convenience.
19 | The humidification control panel shall be at least IP54 rated as standard, with separated electrical and water compartments and be powder coat painted. Casings shall be provided with lockable front access doors permitting full access to all compartments and with sufficient ventilation to prevent overheating
20 | The air-lines and water lines shall include automatic pressure regulating valves, pressure gauges, water modulating valves, solenoid valves and pressure switches.
21 | The units shall be suitable for connecting to the works electrical supply.
22 | The electrical compartment shall have secondary panel cover and all terminals shall be shrouded.
23 | The humidifier shall be supplied with a programmable microprocessor controller including 5 year memory battery back-up, analogue output short circuit proof wiring and real time clock.
24 | The unit shall include a service due hour counter and real time hour counter to ensure automatic maintenance alerts
25 | The unit shall be designed for connection to a 22mm water supply unless otherwise stated.
26 | The system shall incorporate an automatic blow-down technique to empty the water lines of all liquid on shut down to prevent freezing
27 | The system shall be capable of interface with the BMS / controls system / control panel with the necessary monitoring and control functions as indicated elsewhere. The Contractor shall be responsible to ensure co-ordination between all parties.
17.3 | HUMIDIFIER SECTION
A. | General: Capacities and selection in accordance with AHRI 610 (I-P). | Comply |  | Comply in accordance with AHRI 640
B. | Steam Humidifier:
1 | Stainless steel distribution tube with evenly spaced orifices extended full width of unit, factory mounted in plenum with drain pan for draw-through units. | Comply |  | Stainless steel distribution tube with evenly spaced orifices extended full width of unit (Comply), factory mounted in plenum with drain pan for draw-through units (AHU manufacturer Scope).
2 | Humidifiers shall be of the electric steam generator type with lances mounted in stainless steel sections of air handling units. The stainless steel section shall have sufficient up-stream and downstream length to permit full evaporation of the injected | Comply |  | Humidifiers shall be of the electric steam generator type(Comply with Immersed Electrode Humidifier) with lances mounted in stainless steel sections of air handling units. The stainless steel section shall have sufficient up-stream and downstream length to permit full evaporation of the injected (AHU manufacturer Scope)
3 | Injection lances shall be made of stainless steel and shall be mounted horizontally in the airflow, and connected to the steam generator with insulated hose. | Comply |  | Comply with SS linear steam distibutor. Steam hose is not insulated (Steam Hose made of food quality and odorless thermoplastic rubber with galvanized steel helix and polyester yarn reinforcement.)
4 | The steam generator unit shall be housed in a steel cabinet. A separate compartment shall contain the electrical power and control equipment. The cabinet shall have an electro-plated epoxy painted finish and hinged access doors. | Comply with Cabinet housing (carbon steel) | consist of elettrogalvanized sheet 1.2mm. | Comply with Cabinet housing (carbon steel) consist of elettrogalvanized sheet 1.2mm.
5 | Humidifiers shall provide proportional control of steam output and all control systems shall be on-board and provided by the manufacturer. The BMS/control system shall initiate and halt the humidification function as an operator command. Once commanded the on-board humidifier controls shall be self-contained and shall act to achieve the humidity set point. | Comply. For BMS, Modbus Rs485 is standard while (Bacnet is optional with additional price) |  | Comply. For BMS, Modbus Rs485 is standard while (Bacnet is optional with additional price)
6 | Each humidifier cabinet shall have the following features:
a. | Digital display of humidity in space. | Comply through the LCD graphic display |  | Comply through the LCD graphic display
b. | Digital display of humidity set point. | Comply through the LCD graphic display |  | Comply through the LCD graphic display
c. | Digital display of steam output (kg/hour). | Comply through the LCD graphic display |  | Comply through the LCD graphic display
d. | Manual override of steam output. | Comply through the LCD graphic display |  | Comply through the LCD graphic display
e. | Electronic drain timer to control drain cycle for automatic control of minerals. | Comply through the LCD graphic display |  | Comply through the LCD graphic display
f. | High water level warning. | Comply with Different technology using the Conductivity Sensor |  | Comply with Different technology using the Conductivity Sensor
g. | Over current warning. | Comply through the LCD graphic display |  | Comply through the LCD graphic display
h. | Common warning signal to BMS/controls. | Comply |  | Comply
i. | Facility for transmitting space humidity values to BMS. | Comply (If working as stand alone only, not getting a command from BMS ). |  | Comply (If working as stand alone only, not getting a command from BMS ).
7 | Provide as spare parts 1 cylinder and 1 electrode heating element. | Comply with additional price |  | Comply with additional price
17.4 | HUMIDIFIER SECTION
A. | General: Capacities and selection in accordance with AHRI 610 (I-P).
B. | Steam Grid Humidifier:
1. | Stainless steel distribution tube with evenly spaced orifices extended full width of unit, factory mounted in plenum with drain pan for draw-through units.
2. | See Section 23 84 15.
17.5 | 2.1 ELECTRODE STEAM HUMIDIFIERS
A. | General Description: Self-contained, maintainable cylinder or chamber, microprocessorcontrolled electrode steam-generating humidifier, with controls and steam distributor for duct mounting UL listed and CSA certified. | Self-contained, maintainable cylinder or chamber, microprocessorcontrolled electrode steam-generating humidifier, with controls and steam distributor for duct mounting (Comply with HumiSteam X-plus) UL listed and CSA certified. Comply with cETLus (UL standards) and CE
B. | Cabinet: Enclose components in an 18-gauge steel cabinet with enamel or powder coat finish and key-lockable hinged doors for access to plumbing and electrical compartments. | Comply with 1.2 mm galvanized steel
C. | Steam-Generating Cylinders or Chamber:
1. | Cleaning type that can be taken apart for inspection, cleaning, and parts replacement, arranged to generate and discharge steam without mineral carryover. | Comply with Humisteam X-plus
2. | Provide automatically or manually field adjustable maximum electrode output. | Comply with Humisteam X-plus
3. | Furnish one replacement cylinder for each circuit of each humidifier. | Comply with Humisteam X-plus (Additional price for the spare cylinders)
D. | Plumbing Components:
1. | Construct internal plumbing components and valve bodies of high-impact, temperature-resistant plastic or stainless steel, linked with flexible rubber hose. | Comply
2. | Include an air gap on the fill water line to prevent back-siphoning and an integral air gap on the drain side to comply with plumbing codes. | Comply with water inlet via solenoid valve with air gap greater than 25 mm (1”) or double-check valve to prevent backward contamination
3. | Incorporate a built-in strainer, pressure-reducing and flow-regulating orifice into the fill solenoid valve. | Incorporate a built-in strainer (Comply with water cartridge filter), pressure-reducing and flow-regulating orifice into the fill solenoid valve (Not comply).
E. | Steam Distributors:
1. | Stainless steel steam dispersion tubes for duct or air handler mounting, sized to distribute steam uniformly over the entire duct or air handler width. Incorporate a condensate separator and return leg to remove condensate from each steam distributor. | Comply with Humisteam X-plus
2. | Provide hardware for connection between the cabinet steam outlet and the steam distributors. | Comply with rubber hose
F. | Controls:
1. | Description: Microprocessor-based, auto-adaptive control system with proportional plus integral control built-in diagnostics including but do not limit control functions to the following. | Comply
2. | Capacity Control: Full modulating control to provide from zero to 100 percent steam generating capacity. Interrupt power to electrodes when humidity sensors are satisfied. | Comply with Humisteam X plus 20%-100% for UE045 and less and 10-100% for UE065 and more
3. | Fill and Drain Cycle:
a. | Self-regulating for automatic control of mineral (conductivity) buildup to maximize cylinder life and minimize energy waste. | Comply through conuctivity sensor
b. | Electrical and controls to be per Controls Requirements for Packaged Equipment. | Comply
c. | Provide control panel, UL–approved, NEMA 12 enclosure (unless otherwise specified), mounted on the unit, at an accessible location. | Comply with IP20 (Inside the humidifier cabinet)
d. | Provide interface signals to the FMCS: Auto status, run/operating status, general failure, remote start/stop, and other signals as recommended by Vendor. | Comply
e. | Incorporate a high-water probe to prevent overfilling. | Comply with Different technology using the Conductivity Sensor
f. | Automatically drain the cylinder water during periods of prolonged inactivity. Resume normal operation on call for humidity. | Comply
g. | Open the fill valve and temper drain water before it leaves the humidifier. | Open the fill valve (Comply) and temper drain water before it leaves the humidifier (Comply with additional price).
4. | Multiple Cylinder Units: Provide duplicate internal control circuitry and components to allow redundant operation with control circuits coupled to control multiple cylinders from a single control signal. | Comply
5. | Abnormal Condition Controls:
a. | Incorporate self-diagnostic controls circuitry capable of monitoring abnormal conditions and preventing unsafe operation of the unit, including, but not limited to, the following: | Comply
1) | Provide automatic protection from excess electrode current and high-water overflow. | Comply (Through Alarm display)
2) | Shut the humidifier off when the cylinder is full and display cylinder replacement required. | Comply (Through Alarm display)
G. | Electrical:
1. | Provide built-in contactors/starters and internal fused protection on the primary voltage lines. | Comply
2. | Incorporate transformer to step down power for electrical for low-voltage controls. | Comply
3. | Voltage to be 400/50/3. | Comply
H. | Control Features:
1. | Duct-Mounted Humidistat: Solid-state electronic sensor/controller with built-in set point for modulating continuous control of steam flow. Range 10 to 100 percent relative humidity. | Comply with humidity probe. (Humidistat is contractor Scope)
2. | Airflow Proving Switch: Duct-mounted pressure differential switch with adjustable 1.5 mm to 300 mm (0.07 to 12 inches) WC range to shut down the humidifier when no airflow exists. | Contractor Scope
3. | VAV Modulation Control Package: When the steam distributor is located in a duct with varying psychrometrics or air volume, arrange controls to adjust the humidifier capacity to reduce the possibility of saturation and condensation of moisture within the duct. | Contractor Scope

## 18. EC Plug Fans
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
2.12 | FANS
A. | Fans shall have the duty as stated elsewhere when operating at a maximum of 50Hz. | Comply
B. | All fan resistances stated have been calculated based on a particular selection of equipment.
The final selection of plant duties by the Contractor, such as filters, coils, attenuators, diffusers etc., and the actual ductwork fabrication drawings may produce different pressure drops and therefore the Contractor shall recalculate the total system resistances based on the final selection of plant and revise the fan resistance as necessary to achieve the design air volume flow.
C. | Similarly, if the fan power requirements and sound power level changes, the Contractor shall reselect the necessary motor size, wiring and suitable attenuation to achieve the designed noise rating level stated elsewhere at no additional cost.
D. | Selection of fans shall take into account the factors influencing noise levels, including fan speed, velocities, inlet and discharge conditions.
E. | Any allowances required to meet manufacturing and testing tolerances shall be included.
F. | Outlet velocities shall not exceed 10 m/s unless indicated otherwise.
G. | Fan drives or impellers shall be arranged to allow a 10% variation in airflow either volume flow rate or pressure drop for final site adjustment as agreed with the CA. A set of replacement belts and pulleys shall be provided and fitted where required at no additional cost to the contract.
H. | All fans shall be tested in accordance with BS EN ISO 5801:2008, BS 848-1:2007 and BS ISO 13347. Fan impellers shall be statically and dynamically balanced at the works of the manufacturer and test certificates issued to the CA.
I. | Manufacturer’s test certificates, acoustic data and fan curves shall be submitted to the CA. Fan curves shall indicate performance under all likely operating conditions.
J. | Fan resistances shall take account of pressure drop across filters in dirty conditions.
K. | Centrifugal fans shall be belt-driven unless otherwise stated.
L. | Fans shall generally be of the high efficiency (minimum 75% efficiency) backward curved bladed type, double inlet double width and for casings shall be of the lock-form casing type, all welds heavy sheet steel, or split flanged type on the larger fans, adequately braced and stiffened with steel angle with the bottom of the discharge outlet level with the axis of the impeller.
M. | A bolted on access door shall be provided on the fan scroll to allow inspection and cleaning of the impeller. Inlet eyes shall be of the curved aerofoil profile to streamline the airflow into the impeller and of adequate diameter to allow withdrawal of impeller without splitting the fan scroll split cased fans shall be assembled on site by a qualified millwright to ensure that the fan set is correctly assembled and aligned. A drain plug shall be fitted at the base of the fan scroll.
N. | The fan outlet shall be a spigot connection to suit connections to the ductwork system flexible connections within the fan section, or externally, depending on the anti-vibration requirements stated elsewhere.
O. | The fan supporting side frame shall be constructed in angle frame or steel plate and shall be fixed to the fan casing to provide the required angle for the fan discharge arrangement shown elsewhere.
P. | Impellers shall be of welded steel constructed on a case steel hub suitable bored and key-wayed for mounting the shaft and shall have high grade steel plate aerofoil blades or stitched welded to a rigid back plate. The impeller shaft shall be of solid high grade steel adequately sized such that its first critical speed is not reached before the design fan speed is obtained. The fan shaft shall be supported at each side of the impeller with either sealed for life bearing or double roller bearings.
Q. | The shaft shall be connected to the motor drive by cast steel machined pulleys, key-wayed and fixed onto the far and drive shaft by an Approved manner and a multi Vee belt drive arrangement complete with a protective wire guard. The motor shall be a TEFC type mounted on adjustable sliding rails.
R. | The fan casing, side frames, bearing supports and motor shall all be mounted on a heavy steel one piece channel on hollow section base frame and supported on independent spring type anti-vibration mountings, within the fan section as selected by the AHU manufacturer and in accordance with anti-vibration details contained elsewhere in this specification.
S. | The fan sections shall be complete with an approved reinforced steel base to facilitate maintenance within the fan section.
T. | Fan Construction:
1 | Blades of the fans shall be from galvanized steel.
2 | Backward fan's blades shall be treated with epoxy paint.
3 | Wheels shall be statically and dynamically balanced within fan operating speed in compliance to DIN IS0 Standard 1940.
4 | Standard fan bearings shall be "eccentric clamp bearing" type, single row ball bearing, mounted in pressed steel housing, pre-lubricated and sealed for life.
5 | Reinforced fan bearings shall be "self-aligning double rows ball bearing", mounted in cast iron housing and re-greaseable.
6 | Bearing's nominal life expectancy shall be 40,000 L10 operating hours (in accordance with DIN ISO 281 Section-1). Rated bearing life can reach up to 200,000 L10 hours.
U. | Belt drives
1 | Belt drives shall comply with BS 3790 and be capable of transmitting at least the rated power output of the driving motor at any stage of operation with one belt removed. Unless otherwise indicated, not less than two belts per drive shall be used and all multi-belt drives shall use matched sets. Belts shall be of rubber and fibre V section unless otherwise indicated.
2 | Pulleys shall be correctly aligned in accordance with the manufacturer's requirements.
3 | Where duplicate motors are provided and fixed, the spare motor shall be complete with an adjusting device to allow belt tensioning and shall be in all respects ready for operation. The centre-to-centre dimensions between the common driven pulley and the duplicate driving pulleys shall be the same.
4 | Provision shall be made to permit drive alignment and adjustment of belt tension.
V. | Guards
1 | All power transmission shafts, belts and pulley drives shall be guarded and be in compliance with PD 5304.
2 | Fan guards shall be purpose-made by the air handling unit manufacturer or to the approval of the air handling unit manufacturer and be constructed from galvanised or plastic coated steel wire.
3 | Guards shall be installed to prevent inadvertent contact with dangerous parts of machinery and the mesh size and/or the location of the guard shall prevent finger contact with any enclosed danger point.
4 | Construction and installation shall ensure strength and rigidity and it shall not be possible to remove any guard or access panel without the aid of a tool.
5 | Removable access panels shall be provided to permit tachometer readings to be made of motor and drive shafts and belt tension to be tested.
6 | Guards shall be designed for the extreme motor position.
7 | For duplicate motor installations, the guard provided shall be designed to protect both drives. All fixings and mountings shall be installed to facilitate change-over of the drive.
W. | Fan Motors and drives
1 | All motors shall comply with BS 4999, BS 5000, and BS EN 60034 and shall be of such a size and type to start and drive the equipment under normal conditions of service without overloading.
2 | Where mounted in external air, or highly moisture laden atmosphere, they shall be weatherproof or separately protected and shall be a minimum of IP55.
3 | Motors in hazardous atmospheres shall be flameproof, certified to BS EN 60079.
4 | Motors shall comply with other relevant sections of this specification.
5 | Fan motor shall be suitable to operate with Variable Frequency Drive (VFD).
6 | Standard fan's motor shall be a Totally Enclosed Fan Cooled type (TEFC).
7 | Motor's frame shall be from aluminium or cast iron.
8 | Motor shall be able to operate at 50°C operating temperature unless stated otherwise elsewhere.
9 | All motors shall be provided with thermal overload protection "Normally Closed Thermostat" (PTO) as a standard accessory.
10 | Nameplates shall be positioned so that they are readable from normal access positions.
11 | Motors arranged for automatic starting shall have a label of durable material, not less than 150mm x 100mm in size, permanently affixed in a prominent position and having, in clearly inscribed characters, the legend:
a. | Danger - This motor is automatically controlled and may start without warning. Isolate before inspection.
12 | All final motor selections shall be agreed with the CA prior to any equipment being ordered
13 | Vee-belt drives shall comply with BS 3790. A minimum of two belts shall be provided and the drive sized so that the rated output of the motor can be transmitted with one belt removed. A complete set of spare belts shall be provided.
X. | Fan and Motor Mounting Frame:
1 | The fan and motor shall be installed on a common base frame.
2 | The base frame shall be fabricated from heavy gauge galvanized steel.
3 | Motor rail shall be a slide rail type for flexible belt tensioning.
4 | The base frame shall be isolated from floor panel with anti-vibration spring isolator.
5 | The fan shall be isolated to discharge panel with flexible fan connection.
Y. | Variable speed drives
1 | Variable speed drives shall be provided where indicated.
2 | Variable speed motors, drives, control gear and accessories shall be selected by a specialist variable speed drive manufacturer as a complete package. The specialist shall ensure that the unit is capable of providing sufficient power and torque to enable the driven unit to start and operate properly throughout the speed range. The drive shall be capable of providing the additional capacity as indicated elsewhere.
3 | The system shall be capable of interface with the BMS / controls system / control panel with the necessary monitoring and control functions as indicated elsewhere. The Contractor shall be responsible to ensure co-ordination between all parties.
4 | The drive manufacturer, controls specialist and commissioning engineers shall co-ordinate the setting to work of the variable speed drives.
5 | Equipment shall be provided to maintain radio frequency interference and mains harmonic distortion within acceptable levels as indicated elsewhere.
6 | Drives shall be the inverter type. Provision shall be made for the controllers to be by-passed in the event of failure and the equipment manually operated at full speed. Inverters shall be pulse width modulation type, complete with short circuit, earth fault, over voltage, under voltage and over temperature protection. Inverter drives shall provide soft start facilities.
7 | Motors shall be selected with sufficient capacity to allow operation at any point in their curve with overheating limited so that the motor remains within its insulation classification.
8 | Inverters shall be adequately ventilated, by natural means if practical, so that the temperature remains within the normal operating range.
9 | Noise and vibration emission from the equipment shall be treated to ensure that the system complies with the acoustic and vibration requirements stated elsewhere.
10 | Inverters shall have the following characteristics:
a. | Starting current not to exceed full load starting current
b. | Near unit power factor throughout the speed range without the use of power factor correction equipment
c. | Independently adjustable ramp control for increase/decrease speeds
d. | Capable of connecting to a reverse wind milling fan without causing tripping and able to return to correct speed
e. | Local control operation capability
f. | Facility to set all operating parameters with door closed and without the use of additional instrumentation
g. | Provide the following protection:
h. | Motor phase to phase and earth fault
i. | Over voltage and under voltage
j. | Inverter and motor overheat
k. | Stall protection
l. | Loss of control signal and auxiliary control voltage
m. | Current limit by electronic shutdown prior to fuse action
n. | Provide digital readout for :
o. | Output frequency
p. | Hand or auto mode
q. | Motor current
r. | Torque
s. | Power
t. | DC link voltage
u. | Temperature
v. | Fault memory
w. | Provide remote monitoring of all operating conditions and full control capability
11 | Enclosure construction shall provide protection of appropriate IP rating to BS EN 60529.
12 | Inverters shall be CE marked to meet EMC requirements.
2.3 | FANS
A. | The final selection of plant duties by the installer, such as filters, coils, attenuators, diffusers etc., and the actual ductwork fabrication drawings may produce different pressure drops and therefore the installer shall recalculate the total system resistances based on the final selection of plant and revise the fan resistance as necessary to achieve the design air volume flow.
B. | Fan drives or impellers shall be arranged to allow a 10% variation in airflow either volume flow rate or pressure drop for final site adjustment as agreed with the Engineer. A set of replacement belts and pulleys shall be provided for each AHU and fitted where required at no additional cost to the contract.
C. | All fans shall be tested in accordance with BS 848 - 1 and BS ISO 13347. Fan impellers shall be statically and dynamically balanced at the works of the manufacturer and test certificates issued to the Engineer.
D. | Manufacturer's test certificates, acoustic data and fan curves shall be submitted to the Engineer. Fan curves shall indicate performance under all likely operating conditions.
E. | Centrifugal fans shall be belt-driven unless otherwise stated.
F. | Fans shall generally be of the high efficiency (minimum 75% efficiency) backward curved airfoil bladed type, double inlet double width and for casings shall be of the lock-form casing type, all welds heavy sheet steel, or split flanged type on the larger fans, adequately braced and stiffened with steel angle with the bottom of the discharge outlet level with the axis of the impeller.
G. | Fan Motor: Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."
H. | Fans shall be capable of withstanding the pressures and stresses developed during continuous operation at the selected duty, during starting, during stopping and during speed and duty changes. Belt-driven fans shall be capable of running continuously at 10% in excess of the selected duty speed and shall have a minimum of two belts.
Fan casings shall be rigidly constructed and stiffened and braced where necessary to prevent drumming and vibration.
J. | Fans shall be installed using bolts, nuts and washers with all nuts properly locked and secured. All 'as cast' bearing surfaces for bolt heads and washers shall be machine counterfaced. Holding-down bolts for fans and motors shall be provided with means to prevent the bolts turning when the nuts are tightened. Anti-vibration mountings shall be provided. Fans heavier than 20kg shall be provided with eyebolts or other safe means of lifting.
K. | Fan bearings shall be of a type suitable for the size, speed, loads and discharge angle of the fan and shall be greased/oil ball and/or roller type, oil lubricated sleeve type or sealed type. Bearing housings shall be precision aligned and arranged so that bearings may be replaced without the need for realignment. Bearing housings shall be protected against the ingress of dust. For grease lubricated systems, the bearings shall be provided with grease in the quantity and quality recommended by the bearing manufacturer. Oil lubricated systems shall have an adequate reservoir of oil. All bearing lubricators shall be located to facilitate maintenance.
L. | Provisions shall be made for inspection and removal of internal components including impellers and motors. Casings shall have an access panel incorporating an air seal to facilitate cleaning and maintenance. The inlet and outlet of duct mounted fans shall be flanged to facilitate fixing and removal.
M. | Mounting feet shall be provided where necessary for bolting to a base or supports.
N. | Finishes and materials of construction shall be suitable for the operating conditions. Mild steel components shall be protected against corrosion.
O. | Safe access shall be provided to roof mounted fans for inspection and maintenance.
2.4 | BELT DRIVERS
A. | Belt drives shall comply with BS 3790 and be capable of transmitting at least the rated power output of the driving motor at any stage of operation with one belt removed. Unless otherwise indicated, not less than two belts per drive shall be used and all multi-belt drives shall use matched sets. Belts shall be of rubber and fibre V section unless otherwise indicated.
B. | Pulleys shall be correctly aligned in accordance with the manufacturer's requirements.
C. | Where duplicate motors are provided and fixed, the spare motor shall be complete with an adjusting device to allow belt tensioning and shall be in all respects ready for operation. The centre-to-centre dimensions between the common driven pulley and the duplicate driving pulleys shall be the same.
D. | Provision shall be made to permit drive alignment and adjustment of belt tension.
2.5 | FAN SECTION
A. | Fan-Section Construction (supply and return fans sections as applicable): Beltdriven centrifugal fans, consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, and support structure, equipped with formed-steel channel base for integral mounting of fan, motor, and casing panels. Mount fan scroll, wheel, shaft, bearings, and motor on structural-steel frame, with frame mounted on base with vibration isolation.
B. | Housings: Fabricate from formed- and reinforced-steel panels to form curved scroll housings with shaped cutoff, spun-metal inlet bell, and access doors or panels to allow entry to internal parts and components.
C. | Fan Assemblies: Statically and dynamically balanced and designed for continuous operation at maximum rated fan speed and motor power. Fan wheel shall be double-width, double-inlet type with [backward-curved] [airfoil blades] as indicated.
1 | Plug Fans: Fabricate without fan scroll and volute housing, with steel cabinet.
2 | Backward Inclined: Steel or aluminum construction with curved inlet flange, back plate, backward-curved blades, and cast-iron or cast-steel hub.
3 | Airfoil Wheel: Steel; with smooth, curved inlet flange; back plate; dieformed, hollow, airfoil blades; and cast-iron or cast-steel hub.
4 | Shafts: Hot-rolled steel; turned, ground, and polished, and having keyway to secure to fan wheel hub.
5 | Shaft Bearings: Prelubricated and sealed, self-aligning, pillow-block-type ball or roller bearings with the following:
a. | Rated Bearing Life: ANSI/ABMA STD 9 or ABMA STD 11, L-50 of 200,000 hours.
6. | Belt Drives: Factory mounted, with final alignment and belt adjustment made after installation.
a. | Service Factor Based on Fan Motor: 1.5.
7 | Pulleys: Cast iron or steel with split, tapered bushing, dynamically balanced at factory.
8 | Motor Pulleys: Adjustable pitch, selected so pitch adjustment is at middle of adjustment range at fan design conditions.
9 | Belts: Oil resistant, nonsparking, and nonstatic; matched for multiple belt drives.
10 | Belt Guards: Fabricate to OSHA/SMACNA requirements, 2.7 mm thick, 20-mm diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.
11 | Motor Mount: Adjustable for belt tensioning.
12 | Vibration Control: Install fans on open-spring vibration isolators, PVC coated, minimum 25 mm static deflection, with side snubbers. Allowable vibration tolerances for fan shall not exceed a self-excited vibration maximum velocity of 0.005 m/s (0.20 inch per second) RMS when measured with a vibration meter on bearing caps of machine in vertical, horizontal and axial directions or measured at equipment mounting feet if bearings are concealed.
D. | Fan-Section Source Quality Control: The following factory tests are required.
1 | Sound Power Level Ratings: Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data." Test fans according to ANSI/AMCA 300, "Reverberant Room Method for Sound Testing of Fans." Fans shall bear AMCA-certified sound ratings seal or equivalent relevant BS/EN standards.
2 | Factory test fan performance for flow rate, pressure, power, temperature, rotation speed, and efficiency. Establish ratings according to AMCA 210, "Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating", or equivalent relevant BS/EN standards.
2.04 | FAN SECTION
A. | Fans:
1 | Direct drive EC Plug fans. | Comply
2 | High-performance radial impeller provided with circumferential diffuser mounted on an electronically commutated external rotor. | Comply
3 | Radial impeller shall be made of aluminium with backward curved, airfoil, continuously welded blades. | Comply
4 | Aerodynamically optimised inlet nozzle with bleeder connection for pressure relief shall be made of zinc-coated sheet steel. | Comply
5 | Complete unit shall be statically and dynamically balanced. | Comply
6 | Single width, single inlet. | Comply
7 | Class 1 steel wheels. | Comply
8 | AMCA-rated or European certified equivalent. | Comply
9 | Provide with non-overloading characteristics. | Comply
10 | Provide non-sparking integral spun steel venturie inlet cones. | Comply
11 | Provide Alarm relay with zero-potential change-over contacts. | Comply
12 | Provide Locked-rotor protection. | Comply
13 | Provide Phase failure detection. | Comply
14 | Provide Soft start of motors. | Comply
15 | Provide Mains under-voltage detection. | Comply
16 | Provide Over-temperature protection of electronics and motor. | Comply
17 | Provide Short-circuit protection | Comply
B. | Performance Ratings: Determined in accordance with AMCA 210 and labeled with AMCA Certified Rating Seal or European certified equivalent as .
C. | Fan volumetric performance shall be guaranteed and sample tested to AMCA 210.
D. | Sound Ratings: AMCA 301; tested to AMCA 300 and label with AMCA Certified Sound Rating Seal or European certified equivalent as .
E. | Bearings: .
1 | Maintenance-free ball bearings with permanent lubrication | Comply | Bearings shall be with L10 and with life 40,000 hours | 40,000 L10
F. | Mounting:
1 | Locate fan and motor internally on welded steel base coated with corrosion resistant paint. | Not Applicable
2 | Provide access to motor, drive, and bearings through removable casing panels or hinged access doors. | Not Applicable
3 | Drive motors shall be provided with in-unit anti-vibration mounts. | Not Applicable
4 | Flexible connections to the air outlet shall be located within the air handling unit. | Not Applicable
5 | Mount base on vibration isolators. | Not Applicable
6 | Vibration test in operation and at stand-still. | Not Applicable
G. | Housings: 2.66 mm aluminized steel with plenums integral to general housing and constructed to Class 1 fan standards. | Not Applicable
H. | Motors:
1 | EC external-rotor motor efficiency class shall be IE4 without using magnets, with maintenance-free ball bearings and permanent lubrication. | Comply | EC Plug fans have inbuilt IE5 motors | In the case of EC motors, because the motor and electronics are inseparable, it is not possible to isolate and test the motor alone under the standardized conditions required by IEC for IE classification. "Efficiency level of integrated EC motor equivalent to IE5 according to IEC/TS 60034-30-2:2016.” This phrasing is technically correct and widely accepted in the industry.
2 | Type of protection shall be IP54; soft start; integrated current limitation. | Comply |  | IP 55 Soft start - Complied Current limitation - Complied
3 | Compact integrated electronics: with adjustable PID controller shall meet all relevant EMC directives and all requirements as to circuit feedbacks; require no complicated installation with shielded cables; very low-noise commutation logic; 100 % speed-controllable.
4 | Motors with an output of 750W or higher shall have an RS485/MODBUS RTU interface integrated. | Comply
5 | Air performance measurements shall be carried out on suction side and on chamber test beds. | Comply
6 | In case of multiple parallel arrangement, EC fans shall be wired to an external junction box with disconnect switch, fuse and MODBUS / 0-10 V connection. | Comply
7 | Airflow and/or pressure LCD controller/reader shall be factory fitted and wired.
8 | Control: Integrated control electronics. | Comply
9 | Fan Motor: Thermal overload protected. | Comply
10 | Fan Motor: UL listed and labeled or European certified equal. | Comply
11 | All fan motors shall be suitable for operation in winter and summer external conditions of 0 C degree and 50 C degree respectively. | Comply with Remarks | EC plug fan operating range is as mentioned | K3G400HB4101 (-40*C to 40*C) K3G450PB29N1 (-40*C to 40*C) K3G450PA3103 (-40*C to 45*C)
12 | All motors shall be constructed and routine tested at | Not Applicable
| NEMA MG 1 and duplicate copies of test certificates shall be provided before dispatch. Motor winding insulation shall be to NEMA MG 1, Class F or European certified equal.. | Not Applicable
I. | Drives:
1 | Conform to AMCA 99. | Not Applicable
2 | Aerodynamically optimised inlet nozzle with bleeder connection for pressure relief shall be made of zinc-coated sheet steel. | Not Applicable
J. | Fans and motor assemblies shall be sized to permit a 10 % increase in fan duty above values given in the Schedules by simply changing variable speed drives shall be sized accordingly. Fans shall be selected to be capable of a 20 % increase in rotational speed without approaching the first critical speed of the fan/shaft assembly. | Comply
K. | Fan duties given in the Schedules are based on external airside pressure drops. Ensure and demonstrate that the Air Handling Unit manufacturer has selected fans that are capable of overcoming the airside pressure drops within the Air Handling Unit, and any sound attenuator pressure drops above those allowed for in this Specification, in addition to the external pressure drops stated. Where no return fan is specified, external pressure drops stated include return air system drops. | Not Applicable
L. | Motors within Air Handling Units shall be factory-wired to cable terminal boxes mounted externally on the Air Handling Unit casing. | Not Applicable
M. | All motors shall be constructed and routine tested at factory to NEMA MG 1 and duplicate copies of test certificates shall be provided before dispatch. Motor winding insulation shall be to NEMA MG 1, Class F or European certified equal. | Not Applicable
N. | Wiring Termination: Furnish lugs to match branch circuit conductor quantities, sizes and materials indicated. | Not Applicable
O. | Provide 230 V convenience outlets in fan enclosures for use by maintenance and operations personnel. | Not Applicable
P. | External Motor Junction Box: Factory mount NEMA 4 external junction box and connect to extended motor leads from internally mounted motors. | Not Applicable
Q. | Motor Wiring Conduit: Factory wire fan motor wiring to the unit mounted starter-disconnect and external motor junction box | Not Applicable
R. | Fan Accessories:
1 | Discharge dampers. | Not Applicable
S. | Flexible Duct Connections:
1 | For separating fan, coil, and adjacent sections. | Not Applicable

## 19. Fans
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
19.1 | FANS
A. | Fans shall have the duty as stated elsewhere when operating at a maximum of 50Hz.
B. | All fan resistances stated have been calculated based on a particular selection of equipment. The final selection of plant duties by the Contractor, such as filters, coils, attenuators, diffusers etc., and the actual ductwork fabrication drawings may produce different pressure drops and therefore the Contractor shall recalculate the total system resistances based on the final selection of plant and revise the fan resistance as necessary to achieve the design air volume flow.
C. | Similarly, if the fan power requirements and sound power level changes, the Contractor shall reselect the necessary motor size, wiring and suitable attenuation to achieve the designed noise rating level stated elsewhere at no additional cost.
D. | Selection of fans shall take into account the factors influencing noise levels, including fan speed, velocities, inlet and discharge conditions.
E. | Any allowances required to meet manufacturing and testing tolerances shall be included.
F. | Outlet velocities shall not exceed 10 m/s unless indicated otherwise.
G. | Fan drives or impellers shall be arranged to allow a 10% variation in airflow either volume flow rate or pressure drop for final site adjustment as agreed with the CA. A set of replacement belts and pulleys shall be provided and fitted where required at no additional cost to the contract.
H. | All fans shall be tested in accordance with BS EN ISO 5801:2008, BS 848-1:2007 and BS ISO 13347. Fan impellers shall be statically and dynamically balanced at the works of the manufacturer and test certificates issued to the CA.
I. | Manufacturer’s test certificates, acoustic data and fan curves shall be submitted to the CA. Fan curves shall indicate performance under all likely operating conditions.
J. | Fan resistances shall take account of pressure drop across filters in dirty conditions.
K. | Centrifugal fans shall be belt-driven unless otherwise stated.
L. | Fans shall generally be of the high efficiency (minimum 75% efficiency) backward curved bladed type, double inlet double width and for casings shall be of the lock-form casing type, all welds heavy sheet steel, or split flanged type on the larger fans, adequately braced and stiffened with steel angle with the bottom of the discharge outlet level with the axis of the impeller.
M. | A bolted on access door shall be provided on the fan scroll to allow inspection and cleaning of the impeller. Inlet eyes shall be of the curved aerofoil profile to streamline the airflow into the impeller and of adequate diameter to allow withdrawal of impeller without splitting the fan scroll split cased fans shall be assembled on site by a qualified millwright to ensure that the fan set is correctly assembled and aligned. A drain plug shall be fitted at the base of the fan scroll.
N. | The fan outlet shall be a spigot connection to suit connections to the ductwork system flexible connections within the fan section, or externally, depending on the anti-vibration requirements stated elsewhere.
O. | The fan supporting side frame shall be constructed in angle frame or steel plate and shall be fixed to the fan casing to provide the required angle for the fan discharge arrangement shown elsewhere.
P. | Impellers shall be of welded steel constructed on a case steel hub suitable bored and key-wayed for mounting the shaft and shall have high grade steel plate aerofoil blades or stitched welded to a rigid back plate. The impeller shaft shall be of solid high grade steel adequately sized such that its first critical speed is not reached before the design fan speed is obtained. The fan shaft shall be supported at each side of the impeller with either sealed for life bearing or double roller bearings.
Q. | The shaft shall be connected to the motor drive by cast steel machined pulleys, key-wayed and fixed onto the far and drive shaft by an Approved manner and a multi Vee belt drive arrangement complete with a protective wire guard. The motor shall be a TEFC type mounted on adjustable sliding rails.
R. | The fan casing, side frames, bearing supports and motor shall all be mounted on a heavy steel one piece channel on hollow section base frame and supported on independent spring type anti-vibration mountings, within the fan section as selected by the AHU manufacturer and in accordance with anti-vibration details contained elsewhere in this specification.
S. | The fan sections shall be complete with an approved reinforced steel base to facilitate maintenance within the fan section.
T. | Fan Construction:
1 | Blades of the fans shall be from galvanized steel.
2 | Backward fan's blades shall be treated with epoxy paint.
3 | Wheels shall be statically and dynamically balanced within fan operating speed in compliance to DIN IS0 Standard 1940.
4 | Standard fan bearings shall be "eccentric clamp bearing" type, single row ball bearing, mounted in pressed steel housing, pre-lubricated and sealed for life.
5 | Reinforced fan bearings shall be "self-aligning double rows ball bearing", mounted in cast iron housing and re-greaseable.
6 | Bearing's nominal life expectancy shall be 40,000 L10 operating hours (in accordance with DIN ISO 281 Section-1). Rated bearing life can reach up to 200,000 L10 hours.
U. | Belt drives
1 | Belt drives shall comply with BS 3790 and be capable of transmitting at least the rated power output of the driving motor at any stage of operation with one belt removed. Unless otherwise indicated, not less than two belts per drive shall be used and all multi-belt drives shall use matched sets. Belts shall be of rubber and fibre V section unless otherwise indicated.
2 | Pulleys shall be correctly aligned in accordance with the manufacturer's requirements.
3 | Where duplicate motors are provided and fixed, the spare motor shall be complete with an adjusting device to allow belt tensioning and shall be in all respects ready for operation. The centre-to-centre dimensions between the common driven pulley and the duplicate driving pulleys shall be the same.
4 | Provision shall be made to permit drive alignment and adjustment of belt tension.
V. | Guards
1 | All power transmission shafts, belts and pulley drives shall be guarded and be in compliance with PD 5304.
2 | Fan guards shall be purpose-made by the air handling unit manufacturer or to the approval of the air handling unit manufacturer and be constructed from galvanised or plastic coated steel wire.
3 | Guards shall be installed to prevent inadvertent contact with dangerous parts of machinery and the mesh size and/or the location of the guard shall prevent finger contact with any enclosed danger point.
4 | Construction and installation shall ensure strength and rigidity and it shall not be possible to remove any guard or access panel without the aid of a tool.
5 | Removable access panels shall be provided to permit tachometer readings to be made of motor and drive shafts and belt tension to be tested.
6 | Guards shall be designed for the extreme motor position.
7 | For duplicate motor installations, the guard provided shall be designed to protect both drives. All fixings and mountings shall be installed to facilitate change-over of the drive.
W. | Fan Motors and drives
1 | All motors shall comply with BS 4999, BS 5000, and BS EN 60034 and shall be of such a size and type to start and drive the equipment under normal conditions of service without overloading.
2 | Where mounted in external air, or highly moisture laden atmosphere, they shall be weatherproof or separately protected and shall be a minimum of IP55.
3 | Motors in hazardous atmospheres shall be flameproof, certified to BS EN 60079.
4 | Motors shall comply with other relevant sections of this specification.
5 | Fan motor shall be suitable to operate with Variable Frequency Drive (VFD).
6 | Standard fan's motor shall be a Totally Enclosed Fan Cooled type (TEFC).
7 | Motor's frame shall be from aluminium or cast iron.
8 | Motor shall be able to operate at 50°C operating temperature unless stated otherwise elsewhere.
9 | All motors shall be provided with thermal overload protection "Normally Closed Thermostat" (PTO) as a standard accessory.
10 | Nameplates shall be positioned so that they are readable from normal access positions.
11 | Motors arranged for automatic starting shall have a label of durable material, not less than 150mm x 100mm in size, permanently affixed in a prominent position and having, in clearly inscribed characters, the legend:
a. | Danger - This motor is automatically controlled and may start without warning. Isolate before inspection.
12 | All final motor selections shall be agreed with the CA prior to any equipment being ordered
13 | Vee-belt drives shall comply with BS 3790. A minimum of two belts shall be provided and the drive sized so that the rated output of the motor can be transmitted with one belt removed. A complete set of spare belts shall be provided.
X. | Fan and Motor Mounting Frame:
1 | The fan and motor shall be installed on a common base frame.
2 | The base frame shall be fabricated from heavy gauge galvanized steel.
3 | Motor rail shall be a slide rail type for flexible belt tensioning.
4 | The base frame shall be isolated from floor panel with anti-vibration spring isolator.
5 | The fan shall be isolated to discharge panel with flexible fan connection.
Y. | Variable speed drives
1 | Variable speed drives shall be provided where indicated.
2 | Variable speed motors, drives, control gear and accessories shall be selected by a specialist variable speed drive manufacturer as a complete package. The specialist shall ensure that the unit is capable of providing sufficient power and torque to enable the driven unit to start and operate properly throughout the speed range. The drive shall be capable of providing the additional capacity as indicated elsewhere.
3 | The system shall be capable of interface with the BMS / controls system / control panel with the necessary monitoring and control functions as indicated elsewhere. The Contractor shall be responsible to ensure co-ordination between all parties.
4 | The drive manufacturer, controls specialist and commissioning engineers shall co-ordinate the setting to work of the variable speed drives.
5 | Equipment shall be provided to maintain radio frequency interference and mains harmonic distortion within acceptable levels as indicated elsewhere.
6 | Drives shall be the inverter type. Provision shall be made for the controllers to be by-passed in the event of failure and the equipment manually operated at full speed. Inverters shall be pulse width modulation type, complete with short circuit, earth fault, over voltage, under voltage and over temperature protection. Inverter drives shall provide soft start facilities.
7 | Motors shall be selected with sufficient capacity to allow operation at any point in their curve with overheating limited so that the motor remains within its insulation classification.
8 | Inverters shall be adequately ventilated, by natural means if practical, so that the temperature remains within the normal operating range.
9 | Noise and vibration emission from the equipment shall be treated to ensure that the system complies with the acoustic and vibration requirements stated elsewhere.
10 | Inverters shall have the following characteristics:
a. | Starting current not to exceed full load starting current
b. | Near unit power factor throughout the speed range without the use of power factor correction equipment
c. | Independently adjustable ramp control for increase/decrease speeds
d. | Capable of connecting to a reverse wind milling fan without causing tripping and able to return to correct speed
e. | Local control operation capability
f. | Facility to set all operating parameters with door closed and without the use of additional instrumentation
g. | Provide the following protection:
h. | Motor phase to phase and earth fault
i. | Over voltage and under voltage
j. | Inverter and motor overheat
k. | Stall protection
l. | Loss of control signal and auxiliary control voltage
m. | Current limit by electronic shutdown prior to fuse action
n. | Provide digital readout for :
o. | Output frequency
p. | Hand or auto mode
q. | Motor current
r. | Torque
s. | Power
t. | DC link voltage
u. | Temperature
v. | Fault memory
w. | Provide remote monitoring of all operating conditions and full control capability
11 | Enclosure construction shall provide protection of appropriate IP rating to BS EN 60529.
12 | Inverters shall be CE marked to meet EMC requirements.
19.2 | FANS
A. | The final selection of plant duties by the installer, such as filters, coils, attenuators, diffusers etc., and the actual ductwork fabrication drawings may produce different pressure drops and therefore the installer shall recalculate the total system resistances based on the final selection of plant and revise the fan resistance as necessary to achieve the design air volume flow.
B. | Fan drives or impellers shall be arranged to allow a 10% variation in airflow either volume flow rate or pressure drop for final site adjustment as agreed with the Engineer. A set of replacement belts and pulleys shall be provided for each AHU and fitted where required at no additional cost to the contract.
C. | All fans shall be tested in accordance with BS 848 - 1 and BS ISO 13347. Fan impellers shall be statically and dynamically balanced at the works of the manufacturer and test certificates issued to the Engineer.
D. | Manufacturer's test certificates, acoustic data and fan curves shall be submitted to the Engineer. Fan curves shall indicate performance under all likely operating conditions.
E. | Centrifugal fans shall be belt-driven unless otherwise stated.
F. | Fans shall generally be of the high efficiency (minimum 75% efficiency) backward curved airfoil bladed type, double inlet double width and for casings shall be of the lock-form casing type, all welds heavy sheet steel, or split flanged type on the larger fans, adequately braced and stiffened with steel angle with the bottom of the discharge outlet level with the axis of the impeller.
G. | Fan Motor: Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."
H. | Fans shall be capable of withstanding the pressures and stresses developed during continuous operation at the selected duty, during starting, during stopping and during speed and duty changes. Belt-driven fans shall be capable of running continuously at 10% in excess of the selected duty speed and shall have a minimum of two belts.
Fan casings shall be rigidly constructed and stiffened and braced where necessary to prevent drumming and vibration.
J. | Fans shall be installed using bolts, nuts and washers with all nuts properly locked and secured. All 'as cast' bearing surfaces for bolt heads and washers shall be machine counterfaced. Holding-down bolts for fans and motors shall be provided with means to prevent the bolts turning when the nuts are tightened. Anti-vibration mountings shall be provided. Fans heavier than 20kg shall be provided with eyebolts or other safe means of lifting.
K. | Fan bearings shall be of a type suitable for the size, speed, loads and discharge angle of the fan and shall be greased/oil ball and/or roller type, oil lubricated sleeve type or sealed type. Bearing housings shall be precision aligned and arranged so that bearings may be replaced without the need for realignment. Bearing housings shall be protected against the ingress of dust. For grease lubricated systems, the bearings shall be provided with grease in the quantity and quality recommended by the bearing manufacturer. Oil lubricated systems shall have an adequate reservoir of oil. All bearing lubricators shall be located to facilitate maintenance.
L. | Provisions shall be made for inspection and removal of internal components including impellers and motors. Casings shall have an access panel incorporating an air seal to facilitate cleaning and maintenance. The inlet and outlet of duct mounted fans shall be flanged to facilitate fixing and removal.
M. | Mounting feet shall be provided where necessary for bolting to a base or supports.
N. | Finishes and materials of construction shall be suitable for the operating conditions. Mild steel components shall be protected against corrosion.
O. | Safe access shall be provided to roof mounted fans for inspection and maintenance.
19.3 | BELT DRIVERS
A. | Belt drives shall comply with BS 3790 and be capable of transmitting at least the rated power output of the driving motor at any stage of operation with one belt removed. Unless otherwise indicated, not less than two belts per drive shall be used and all multi-belt drives shall use matched sets. Belts shall be of rubber and fibre V section unless otherwise indicated.
B. | Pulleys shall be correctly aligned in accordance with the manufacturer's requirements.
C. | Where duplicate motors are provided and fixed, the spare motor shall be complete with an adjusting device to allow belt tensioning and shall be in all respects ready for operation. The centre-to-centre dimensions between the common driven pulley and the duplicate driving pulleys shall be the same.
D. | Provision shall be made to permit drive alignment and adjustment of belt tension.
19.4 | FAN SECTION
A. | Fan-Section Construction (supply and return fans sections as applicable): Beltdriven centrifugal fans, consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, and support structure, equipped with formed-steel channel base for integral mounting of fan, motor, and casing panels. Mount fan scroll, wheel, shaft, bearings, and motor on structural-steel frame, with frame mounted on base with vibration isolation.
B. | Housings: Fabricate from formed- and reinforced-steel panels to form curved scroll housings with shaped cutoff, spun-metal inlet bell, and access doors or panels to allow entry to internal parts and components.
C. | Fan Assemblies: Statically and dynamically balanced and designed for continuous operation at maximum rated fan speed and motor power. Fan wheel shall be double-width, double-inlet type with [backward-curved] [airfoil blades] as indicated.
1 | Plug Fans: Fabricate without fan scroll and volute housing, with steel cabinet.
2 | Backward Inclined: Steel or aluminum construction with curved inlet flange, back plate, backward-curved blades, and cast-iron or cast-steel hub.
3 | Airfoil Wheel: Steel; with smooth, curved inlet flange; back plate; dieformed, hollow, airfoil blades; and cast-iron or cast-steel hub.
4 | Shafts: Hot-rolled steel; turned, ground, and polished, and having keyway to secure to fan wheel hub.
5 | Shaft Bearings: Prelubricated and sealed, self-aligning, pillow-block-type ball or roller bearings with the following:
a. | Rated Bearing Life: ANSI/ABMA STD 9 or ABMA STD 11, L-50 of 200,000 hours.
6. | Belt Drives: Factory mounted, with final alignment and belt adjustment made after installation.
a. | Service Factor Based on Fan Motor: 1.5.
7 | Pulleys: Cast iron or steel with split, tapered bushing, dynamically balanced at factory.
8 | Motor Pulleys: Adjustable pitch, selected so pitch adjustment is at middle of adjustment range at fan design conditions.
9 | Belts: Oil resistant, nonsparking, and nonstatic; matched for multiple belt drives.
10 | Belt Guards: Fabricate to OSHA/SMACNA requirements, 2.7 mm thick, 20-mm diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.
11 | Motor Mount: Adjustable for belt tensioning.
12 | Vibration Control: Install fans on open-spring vibration isolators, PVC coated, minimum 25 mm static deflection, with side snubbers. Allowable vibration tolerances for fan shall not exceed a self-excited vibration maximum velocity of 0.005 m/s (0.20 inch per second) RMS when measured with a vibration meter on bearing caps of machine in vertical, horizontal and axial directions or measured at equipment mounting feet if bearings are concealed.
D. | Fan-Section Source Quality Control: The following factory tests are required.
1 | Sound Power Level Ratings: Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data." Test fans according to ANSI/AMCA 300, "Reverberant Room Method for Sound Testing of Fans." Fans shall bear AMCA-certified sound ratings seal or equivalent relevant BS/EN standards.
2 | Factory test fan performance for flow rate, pressure, power, temperature, rotation speed, and efficiency. Establish ratings according to AMCA 210, "Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating", or equivalent relevant BS/EN standards.
19.5 | FAN SECTION
A. | Type: Air foil, vane axial plug fan, in accordance with AMCA 99. See Section 23 34 13
B. | Performance Ratings: Determined in accordance with AMCA 210 and labeled with AMCA Certified Rating Seal.
C. | Sound Ratings: AMCA 301; tested to AMCA 300 and label with AMCA Certified Sound Rating Seal.
D. | Bearings: Self-aligning, grease lubricated, with lubrication fittings extended to exterior of casing with copper tube and grease fitting rigidly attached to casing.
E. | Mounting:
1. | Locate fan and motor internally on welded steel base coated with corrosion resistant paint.
2. | Factory mount motor on slide rails.
3. | Provide access to motor, drive, and bearings through removable casing panels or hinged access doors.
F. | External Motor Junction Box: Factory mount NEMA 4 external junction box and connect to extended motor leads from internally mounted motors.
G. | Motor Wiring Conduit: Factory wire fan motor wiring to the unit mounted starter-disconnect, variable frequency drive, and external motor junction box.
H. | Fan Accessories:
I. | Flexible Duct Connections:
1. | For separating fan, coil, and adjacent sections.
J. | Drives:
1. | Direct Drive Comply with AMCA 99.

## 20. Motors
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
2.1 | MOTORS
A. | General: Refer to Section "Common Motor Requirements for HVAC Equipment" for general requirements.
B. | Provide internally vibration isolated fan, motor and drive, mounted on a common integral bolted or welded structural steel base with adjustable motor slide rail with locking device. Provide vibration isolators and flexible duct connections at fan discharge to completely isolate fan assembly. Fan drive and belts shall be factory mounted with final alignment and belt adjustment to be made by the Contractor after installation.
C. | Torque Characteristics: Sufficient to accelerate driven loads satisfactorily.
D. | Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range.
E. | Temperature Rating: 50 deg C maximum temperature rise at 40 deg C ambient for continuous duty at full load (Class A Insulation).
F. | Service Factor: 1.15 for polyphase motors and 1.35 for single-phase motors.
G. | Motor Construction: ANSI/NEMA MG 1, general purpose, continuous duty, Design B, or equivalent characteristics in accordance with relevant parts of IEC 60034, or equivalent relevant en/BS standards.
1 | Bases: Adjustable.
H. | Bearings: The following features are required:
1 | Ball or roller bearings with inner and outer shaft seals.
2 | Grease lubricated.
3 | Designed to resist thrust loading where belt drives or other drives produce lateral or axial thrust in motor.
I. | Enclosure Type: The following features are required:
1 | Open dripproof motors where satisfactorily housed or remotely located during operation.
2 | Guarded dripproof motors where exposed to contact by employees or building occupants.
J. | Overload Protection: Built-in, automatic reset, thermal overload protection.
K. | Noise Rating: Quiet.
L. | Efficiency: Energy-efficient motors shall have a minimum efficiency as scheduled according to IEEE 112, Test Method B. If efficiency is not specified, motors shall have a higher efficiency than "average standard industry motors" according to IEEE 112, Test Method B.
M. | Nameplate: Indicate full identification of manufacturer, ratings, characteristics, construction, and special features.
N. | Starters, Electrical Devices, and Wiring: Electrical devices and connections are specified in Division 26 Sections.

## BLDC vs EC motors
Category | DC Motor (Brushed DC) | BLDC Motor (Brushless DC) | EC Motor (Electronically Commutated)
Definition | Electromechanical motor with mechanical commutation (brushes + commutator). | Brushless motor with electronic commutation using external driver/controller. | Essentially a BLDC motor with integrated electronics (controller + protections + communication).
Commutation Method | Mechanical (brushes/commutator). | Electronic, through external drive/ESC. | Electronic, built‑in drive optimized for application.
Construction | Rotor windings + brushes; stator magnets. | Stator windings + rotor permanent magnets. No brushes. | Same BLDC construction + integrated electronics in housing.
Control Electronics | Not required (direct power control). | Required; separate driver defines performance. | Built‑in; optimized and pre-tuned.
Speed Control | Easy, via voltage variation (linear). | Wide range; PWM or feedback control via external drive. | Built-in: 0–10 V, PWM, Modbus/BACnet/CAN (depends on model).
Efficiency | Low to moderate; losses from brush friction and heat. | High; depends on controller quality. | High and consistent; integrated controller optimizes commutation + PFC for mains models.
Torque Characteristics | High starting torque; smooth. | High torque; dynamic response dependent on tuning. | Designed for stable torque delivery for fans, pumps, HVAC.
Noise Level | High (brush noise + ripple). | Low (sinusoidal controllers), moderate on cheap trapezoidal drives. | Very low; optimized sinusoidal commutation.
Maintenance | High—brush wear, dust, arcing. | Low—no brushes. | Very low—sealed electronics + no brushes.
Lifespan | Limited by brush wear. | Long lifespan. | Long lifespan; minimal wear parts.
EMI/EMC | Arcing from brushes creates EMI. | EMI depends on controller and wiring. | Optimized EMC filtering inside the motor.
Thermal Handling | Heat at brushes and windings. | Motor + controller heat handled separately. | Integrated thermal management + protection.
Protections | Minimal inherent protections. | Depends on controller (overload, stall, temp). | Extensive built-in protections.
Power Factor (AC-fed) | Poor unless external electronics added. | Depends on controller; needs PFC module. | Typically includes active PFC for mains supply (HVAC-grade).
Speed Range | Moderate; limited by brushes/commutation. | Very wide; excellent RPM capability. | Wide but optimized for application range.
Reliability | Moderate; mechanical wear. | High. | Very high—factory matched motor + drive.
Cost (Motor) | Low. | Moderate. | Higher due to integrated electronics.
Cost (System) | Low to moderate. | Can vary—needs external driver. | Predictable; higher upfront but low integration cost.
Integration Effort | Very simple; direct wiring. | Requires driver selection + tuning + EMI care. | Very easy; plug‑and‑play.
Typical Interfaces | None or simple analog. | PWM, analog, CAN, RS‑485 (if controller supports). | 0–10 V, PWM, Modbus, BACnet, CAN, potentiometer.
Applications | Toys, simple machines, low-cost drives, automotive accessories. | Robotics, EVs, drones, CNC, automation. | HVAC fans, blowers, pumps, compressors, appliances.
Best When | Cost-sensitive, simple control needed. | High performance and flexibility required. | High efficiency, plug‑and‑play, low noise, regulatory compliance needed.
Summary
| DC Motors | BLDC Motors | EC Motors
| ✔ Simple and cheap | ✔ High efficiency, long life | ✔ BLDC + perfect controller pairing
| ✖ High wear, low lifespan | ✔ Highly configurable using external controllers | ✔ Very quiet, reliable, energy-efficient
| ✖ Not energy-efficient | ✖ Requires engineering for driver selection, tuning, EMC | ✔ Meets HVAC/pump efficiency regulations
| ✔ Good for low-cost consumer and industrial devices |  | ✖ Higher upfront cost
✖ Less customizable

## 21. Nameplate
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
21.1 | NAMEPLATE
A. | Each Air Handling Unit shall be complete with a unique identification reference label (as indicated in project documents) fitted at the manufacturer’s works. The identification reference shall be clearly visible through the wrapping. The text and method of reference shall be as approved by the CA prior to ordering and shall be utilised in the record documentation. In addition to this a securely attach nameplate on each fan coil unit showing manufacturer name, serial, model number etc. is required.

## 22. Quality Control
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
22.1 | QUALITY CONTROL
A. | Factory Tests: In addition to the testing requirements stated elsewhere, standard factory tests shall be performed on each unit and shall be completed and factory certified. The fans shall be factory run tested to ensure structural integrity and proper RPM. All electrical circuits shall be tested to ensure correct operation before shipment of the unit. Units shall pass factory quality control and testing and be thoroughly cleaned prior to shipment.
B. | All sections of the units, including those that are split for shipment, shall be thoroughly cleaned externally and internally prior to wrapping for shipment. All scratches to painted surfaces both inside and out shall be cleaned and repainted and the interior of the unit shall be completely vacuumed to remove all dust, metal shavings or other debris. Wrap each section shipment with suitable protection to ensure delivery free from deterioration.
C. | Witness of Factory Standard Tests: As stated elsewhere the manufacturer shall include a provision for the witnessing of the standard factory tests as described above and inspection during assembly of each air handling unit, fresh air handling unit and heat recovery unit specified for the project.

## 23. Controls
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 2 - PRODUCT
2.09 | CONTROLS
A. | Factory Installed Direct Digital Control (DDC) System:
1. | DDC Controller:
a. | Provide panel-mounted, factory wired, application-specific (ASC) or advanced application-programmable controller (APC).
b. | ASC or APC: See Section 25 14 00 except for manufacturer-provided units that are fully compatible with site BAS, BMS, SCADA, or Integrated Automation System.
c. | Include built-in or provide local screen push-button interface for local monitoring, adjustment, tuning, data logging, and troubleshooting.
d. | Factory configured to handle internal equipment using manufacturer's specific instructions unless directly specified on listed sequence of operation.
e. | Factory wired into panel-mounted auxiliary relay(s) to handle scheduled or interlocked cycle-duty operation of externally linked equipment as indicated on drawings.
f. | Factory installed, wired, programmed, and tested, including each component.
g. | BAS, SCADA, or other Integrated Automation Link: ASHRAE Std 135 BACnet MS/TP.
2. | Mixing Section Dampers:
a. | Outdoor Air Damper: Fail closed using spring-return actuator.
b. | Return Air Damper: Fail open using spring-return actuator.
3. | Temperature Sensors: Provide for fan discharge and return. Use averaging type for coil sections.
4. | Low Limit Switches:
a. | Factory wire to momentary push-button reset circuit.
b. | Provide separate low limit for each coil in a coil stack.
5. | Fan Status: Provide current switch and pressure switch to determine running status.
6. | Loaded Filter Section: Tube to filter section to indicate sectional filter status.
7. | Condensate Overflow Switches:
a. | Comply with UL 508; shut down unit in the event of primary drain blockage.
b. | Factory install float switch in drain pan to detect high water condensate level.
c. | Locate float switch above primary drain line connection and below drain pan rim.
8. | Relays, Unit-Mounted, Output-Linked: Provide for external loads including motor starters, relief dampers, pumps, condensing units, and other equipment as specified in the drawings.
B. | BAS, SCADA, or other Integrated Automation Link: ASHRAE Std 135 BACnet MS/TP.
C. | External Point Mapping: Provide mapping table for each parameter included in the local visual interface with software-toggle flag to allow reduced mapping of available points.

## 24. Execution
Sr | Specifications | Compliance | Remarks | Internal Comments
PART 3 - EXECUTION
24.1 | INSTALLATION
A. | Install in accordance with manufacturer's instructions.
B. | Bolt sections together with gaskets.
C. | Isolate fan section with flexible duct connections.
D. | Install flexible duct connections between fan inlet and discharge ductwork and air handling unit sections. Ensure that metal bands of connectors are parallel with minimum 25 mm flex between ductwork and fan while running.
E. | Install assembled unit on vibration isolators. Install isolated fans with resilient mountings and flexible electrical leads. Install restraining snubbers as indicated; see Section 23 05 48. Adjust snubbers to prevent tension in flexible connectors when fan is operating.
F. | Provide sheaves required for final air balance.
G. | Make connections to coils with unions or flanges.
H. | Hydronic Coils:
1. | Hydronic Coils: Connect water supply to leaving air side of coil (counterflow arrangement).
2. | Provide shut-off valve on supply line and lockshield balancing valve with memory stop on return line.
3. | Locate water supply at bottom of supply header and return water connection at top.
4. | Provide manual air vents at high points complete with stop valve.
5. | Ensure water coils are drainable and provide drain connection at low points.
I. | Cooling Coils:
1. | Pipe drain and overflow to nearest floor drain.
J. | Connect Humidifiers to Water Supply:
1. | Provide gate valve on water supply line.
2. | Provide 20 mm hose bibb accessible from interior.
3. | Pipe drain and overflow to nearest floor drain.
K. | Coordinate BAS, BMS, or Integrated Automation linking between unit controller(s) and remote front-end interface; see Section 25 15 00.
3.02 | FIELD QUALITY CONTROL
A. | See Section 01 40 00 - Quality Requirements for additional requirements.
B. | Vibration Analysis:
1. | Measure vibration levels with an FFT (Fast Fourier Transformation) analyzer.
2. | Characteristics:
a. | Frequency Response Range: 5 Hz thru 10 KHz (300 thru 600,000 cpm).
b. | Capability to use a Hanning window.
c. | Capacity to perform ensemble averaging.
d. | Auto-ranging frequency amplitude.
e. | Minimum amplitude accuracy over the selected frequency range of plus/minus 20 percent or plus/minus 1.5 dB.
3. | Use accelerometer, stud-mounted to collect data.
4. | Ensure the mass of the accelerometer and its mounting have minimal influence on the frequency response of the system over the selected measurement range.
C. | Final Acceptance Requirements:
1. | Use dial indicator gauges to demonstrate fan and motor are aligned.
2. | Verify compliance with specifications using vibration analysis.
3. | Maximum Vibration Levels:
a. | 1.905 mm per second at 1 times run speed and at fan/blade frequency.
b. | 1.016 mm per second at other multiples of run speed.
D. | Coordination of Other Tests and Inspections:
1. | Owner will employ independent Testing, Adjusting, and Balancing agency to test and/or inspect modular central-station air handling-unit.
2. | Provide access and tools as required to accommodate timely performance.
3.03 | SYSTEM STARTUP
A. | Provide manufacturer's field representative to perform systems startup.
B. | Prepare and start equipment and systems in accordance with manufacturers' instructions and recommendations.
C. | Adjust for proper operation within manufacturer's published tolerances.
3.04 | CLOSEOUT ACTIVITIES
A. | See Section 01 78 00 - Closeout Submittals for closeout submittals.
B. | See Section 01 79 00 - Demonstration and Training for additional requirements.
C. | Demonstrate proper operation of equipment to Owner's designated representative.
D. | Demonstration: Demonstrate operation of system to Owner's personnel.
1. | Use operation and maintenance data as reference during demonstration.
2. | Conduct walking tour of project.
3. | Briefly describe function, operation, and maintenance of each component.
E. | Training: Train Owner's personnel on operation and maintenance of system.
1. | Use operation and maintenance manual as training reference, supplemented with additional training materials as required.
2. | Provide minimum of two hours of training.
E. | Training: Train Owner's personnel on operation and maintenance of system.
1. | Use operation and maintenance manual as training reference, supplemented with additional training materials as required.
2. | Provide minimum of two hours of training.